EXECUTIVE SUMMARY:

ADD EXECUTIVE SUMMARY HERE

CONTENTS

PROJECT BACKGROUND AND OVERVIEW……………………………………………………………………..

ABSTRACT……………..…………………………………………………………………………………………………

BUILDING STATISTICS
Part One………………………………………………………………………………………………………
Part Two………………………………………………………………………………………………………

DEPTH | LIGHTING
Overview………………………………………………………………………………………………………
Space One:  Building Façade………………………………………..……………………………….
Space Two: Main Lobby…………………………………….………………………………………..
Space Three: Education and Lecture Room…………………..…………………………….
Space Four: Meeting Room……………………………….………………………………………..

DEPTH | ELECTRICAL
Redesigned Spaces…………..………………………………………..……………………………….
Photovoltaic Array Study……………………………………………………………………………..
120/208V to 277/480V Conversion Study……………………………………………………………
Protective Device Coordination Study…………………………………………………………

BREADTH | ARCHITECTURE
Overview……………………………………………………………………………………………………..
Design Goals…..…………………………………………………………………………………………..
Design Concepts…………………………………………………………………………………………
Final Products……………………………………………………………………………………………..
Analysis…………………………………………………………………………………………………………

BREADTH | ACOUSTICS
Overview……………………………………………………………………………………………………..
Existing Conditions Analysis…………………………………………………………………………
Solution………………………………………………...........................................................

SUMMARY AND CONCLUSIONS……………..……………………………………………………………………..

REFERENCES……………………………………………………………………………………………………………….

ACKNOWLEDGEMENTS…………………………………………………………………………………………………

APPENDICES
A - Luminaire and Ballast Data………………………………………………………………….………
B - Lighting Plans……………………………………………………………………………………………
C - Lighting Performance Data………………………………………………………………………
D - Lighting Renderings…………..……………………………………………………….……....
E - Building Materials……………………………………………………………………………………
F - Existing System Electrical Panels……….………………………………………………..
G - New System Electrical Worksheets and Panels…………………………………….
H - Electrical Plans…………………………………………………………………………………………
I - Existing Single Line Diagram……………………………………………………….………..
J - Redesigned Single Line Diagram…………………………………………………………….
K - Electrical Product Specifications…………………………………………………………….
L - Architectural Images……………………………………………………………………………..

This report, along with addition information, is available in electronic format at: http://www.engr.psu.edu/ae/thesis/portfolios/2008/mpr184/

SECTION ONE | Project Background and Overview

Prominently located on Liberty Avenue, The August Wilson Center for African American Culture is designed to be a signature element of down Pittsburgh architecture.  Rich materials and bold geometric forms set the stage for a magnificent cultural experience that any patron is sure to undergo.  Beyond the aesthetic beauty of the architecture lie structural, mechanical, acoustical, electrical, and lighting systems that must perform precisely and efficiently in order to make the building triumphant.  The synthesis of aesthetics and functionality is the pinnacle of great design.

The project architect, Perkins + Will, describes the August Wilson Center as follows:

Allison Williams, Lead Designer for the architectural firm of Perkins+Will has designed this home for the August Wilson Center as a conceptually transparent, flexible container in which the accomplishments and artifacts, the activities and traditions of this culture can be proudly celebrated layered and displayed. The building opens itself to educating people about the important contribution of African Americans to Pittsburgh and beyond. It is timeless, flexible and powerful in its simplicity.

The signature character of the building comes as a result of its content, in response to the program and is in continuous transformation as a result of the changing exhibits and activities within. It is through the design element at the corner of Liberty Avenue and William Penn Way that the architects position the building as a distinct icon, and abstraction of this culture and a new landmark for Pittsburgh. This is where the August Wilson Center finds its voice, its identity, its energy and its distinct signature quality.

This capstone design project and Architectural Engineering senior thesis involved a substantial analysis of the existing building approach, specifically in the areas of lighting and electrical systems.  This analysis provided goals for redesigning these systems for four spaces:  the Liberty Avenue façade, the main lobby, the education and lecture room and the meeting room/donor lounge.  The systems were redesigned with the purpose of creating enhanced integration between the spaces themselves, the user, and the environment.  Taken from the signature sail element, an attempt was made to  emphasize a nautical or ship theme.

Additional work in architectural design and acoustical systems supplemented this body of work.  Acoustics was identified as an area of concern based on the large volume spaces and many hard surfaces.  As a public space designed for large crowds and with performance paramount, proper acoustical design is essential.  Architecturally, a roof terrace was designed with the goal of further emphasizing the iconic sail feature.

ABSTRACT

SECTION THREE | Building Statistics for Existing Design

GENERAL BUILDING DATA:

Building Name:  August Wilson Center for African American Culture
Location and Site:  Liberty Avenue and William Penn, Pittsburgh, Pennsylvania
Building Occupant Name:  August Wilson Center for African American Culture
Occupancy or Function Types:  The building will open in phases.  The first phase to open will be gallery and display space.  A 500 seat performance theater will be opened second.
Size:  63,000 Square Feet
Number of Stories Above Grade:  Two
Primary Project Team:

Architect:  Perkins + Will (http://www.perkinswill.com)

Engineering:

Civil:  A&A Consultants (http://aaconsultinc.com/)

Structural: Atlantic Engineering Services (http://www.aespj.com)

Consultants:

ARUP (http://www.arup.com)

ATS Chester Engineers (http://www.atschester.com)

Auerbach + Pollack + Friedlander (http://www.auerbackconsultants.com)

Duquesne Light (http://www.duqlight.com)

Hornfeck Engineering (http://www.hornfeck.com)

Middlebrook + Louie (http://www.MplusL.com)

Sextant Group (http://www.thesextantgroup.com)

the studio i company (http://www.studioilighting.com)

Timothy Engineering (http://www.timothyengineering.com)

Construction Management:

Ebony Development, LLC (http://www.ebonydevelopment.com)

Sterling Contracting, LLC (http://www.sterlingcontractingllc.com/)

Turner Construction (http://www.turnerconstruction.com/)

Law Firm:

Buchanan Ingersoll & Rooney, PC (http://www.bipc.com)

Owner’s Representative:

Oxford Development Company (http://www.oxforddevelopment.com)

Dates of Construction: Start Date – August 2, 2007.  Expected Duration – 18 months.
Cost:   The budget cost decided by the owner is 23 million dollars.  The project has come in over budget and value engineering is taking place in order to achieve a final cost that is acceptable to the owner.
Project Delivery Method:   The project began with a GMP contract.  However, it is currently structured as a CM agent with approximately 23-24 prime contracts.

ARCHITECTURAL INFORMATION:

Design and Functional Components:  The program consists of a central performing arts theater surrounded by lobby and gallery space.  There is space allocated for both permanent and temporary exhibits.  There is a café off of the ground floor lobby.  The second level also includes a multi-purpose room, classrooms and an open office area for administrative activities related to the center.

Major National Model Codes:  IBC 2003

Zoning: Commercial

Historical Requirements: None.  The site is owned by the Urban Redevelopment Authority (URA) of Pittsburgh.  Requirements must be met during the demolition and site preparation in order for the ownership to transfer to the August Wilson Center.

Building Envelope:  The building features several exterior wall systems.  The foundation and basement is cast-in-place concrete to grade.  Above grade structural steel with concrete/steel decking and 6” metal stud walls forms the building envelope.  The exterior of the building features several materials including 2” insulated aluminum panel, ACM (Aluminum Composite) panels, ribbed metal panels, aluminum/glass curtain wall, and 8” CMU cavity wall.  These systems are integrated and used in various combinations throughout the building.  The walls are insulated with R19 batt insulation, and surfaced with 5/8” sheathing and waterproof membrane.  The roof is an EPDM system over tapered insulation to provide adequate drainage.  Parapet walls are used as necessary and capped with metal coping.

CONSTRUCTION METHOD:
Turner Construction Company is the primary construction management firm for this project.  The delivery method was original GMP with a project budget of 23.5 million dollars.  When the project came in over budget, the method was switched to CM Agent with Turner as the CM and 23-24 prime contracts between the August Wilson Center and the contractor.  This switch occurred in the summer of 2007.

With a location in downtown Pittsburgh, the site had previously been occupied and it was therefore necessary to complete demolition prior to beginning new construction.  The site was owned by the Pittsburgh Urban Redevelopment Authority (URA).  When excavation began, soil contamination was discovered and the agreement with the URA stated that it must be remedied before the land ownership would be transferred.

A set of permit review drawings was released October 2, 2007.  Due to the late shift in delivery method, Turner had to pre-purchase materials for early bid packages, such as the steel.  The estimated length of construction is 18 months.

ELECTRICAL SYSTEM:

The building runs on a 208Y/120V, 3 phase, 4 wire electrical system and is connected to the Duquesne Light system.  Service enters the building on the south side of the building where two transformers are located.  Each transformer supplies a main switchboard.  One of these switchboards supplies predominantly mechanical and equipment loads while the second switchboard supplies mainly lighting and other end-user loads.

Dimming equipment is necessary to accommodate theatre equipment and is also used for some of the general purpose spaces.  The most unique part of the system is a motorized orchestra pit lift.  However, this piece of equipment is slated to be added at a later time.

A 200KW diesel generator provides emergency power to certain parts of the system through two automatic transfer switches.

LIGHTING STSTEMS:
The building’s lighting system is faced with the challenge of responding to the building’s unique architectural form and varying materials.  With open plenum ceiling that have open grids and vertical metal baffles, indirect lighting is not an option.  Black acoustical blanket on the ceiling means the reflectance is very low.

Regular arrays of round downlights light the upper and lower lobbies.  Accent and interest is provided by varying lighting in the adjacent spaces that connect to the lobby and by highlighting the oval shaped drum of the theater that protrudes through the entire building.

In the gallery spaces track lighting is used to provide a very flexible solution.  Dimming systems are used in spaces such as the education room and meeting room to provide variable light levels.  Motorized blackout shades are used to address the large amounts of daylight that will enter the spaces through the Liberty Avenue Façade.

The exterior lighting design is focused on accenting special elements rather than washing the entire façade.  The building glows from the inside due to the large expanses of clear glass.  The corner sail is highlight from inside and from in-grade recessed fixtures.

MECHANICAL SYSTEM:

Building heating and cooling is handled by five air handling units (condenser capacities: 735, 608, 727, 530, 951 MBH) that are housed on the roof of the structure.   The units contain DX coiling coils and glycol preheat and reheat hot water heating coils.  One of these units is also connected to the backup emergency system.  Four small split AC units serve mechanical and equipment rooms.  Additional heating is provided by electric baseboard heaters in the exhibit hall.

A steam and water room in basement of the building houses plumbing equipment, heating coils and other water related mechanical equipment.

STRUCTURAL SYSTEM:
The foundation of the building is provided by 10 to 12 inch poured concrete foundation walls which rest on grade beams.  Concrete piles are used to support the columns.  The basement level is only a portion of the area of the first level.  On grade floors are concrete slab on grade.  Where the basement level exists, the first floor is a two way structural concrete slab that is 10 inches thick or a 15-20” thick one way slab.

W shape steel columns support the second floor and roof loads.  The column arrangement is not regular due to the generally triangular shape of the overall building and the oval shape of the theater core.  The triangular system is a moment frame construction while the inner oval shape of the theater is a braced frame construction.  Bent beams are used to make the curved theater walls.

The second level floor is framed with structural steel with steel decking and concrete slab.  The roof uses a similar system but is sloped for drainage and includes rigid insulation on top.  The balcony seating area is a series of cantilevered concrete slabs.

FIRE PROTECTION:

With only two stories, the building does not require d to have active fire protection throughout.  Fire protection (1HR)  is provided around egress stairwells and elevators. The theatre stage area has a two hour rating.  Several other walls, including exterior walls bordering other buildings have a one hour rating.  Many of the electrical/mechanical spaces are also protected by a one hour fire rated wall assembly.  Steel is protected by cementious fireproofing where necessary.

The building utilizes a sprinkler system throughout.  A separate water service for the sprinkler system enters the building from the south where a main control system is located.  A dry system is used to protect the two exhibit spaces while a wet system is used for the remainder of the building.

TRANSPORTATION SYSTEM:
The transportation system includes three elevators, one of which is a large elevator that can be used to move equipment.  Only two of these elevators service the basement.  The larger elevator connects through to the basement and two exhibit spaces.

The building has three standard egress stairwells one of which connects the basement.  A grand staircase connects the two lobbies while two staircases provide direct pedestrian access to the balcony seating in the theatre.

A service entrance to the building is located on the south side of the structure and comes off of William Penn Place.  This entrance provides a two bay loading dock with access to the stage area of the main theatre.

TELECOMMUNICATIONS:

The building communication systems consist of standard ethernet, and phone systems with a few items related to projectors and audio systems.  The theatrical communication and audio systems will not be considered for this report.  The main control and distribution panels are located in room 111 on the south side of the building.  This is where service from Verizon enters the building below grade from the street.  A secondary control station, room 211, is located directly above room 111.

The voice and data network runs throughout the building.  This system will provide internet connectivity as well as phone lines to the various building spaces.  This is especially relevant for the open office area.  Various types of outlet boxes are used depending on the constraints of mounting locations.  Everything from wall to floor to ceiling boxes are used, with various numbers of both voice and data jacks mounted together.

The overall audio and video system includes a regular array of speakers located through the lobbies of the building.  Separate audio systems are in place for the café, education/lecture room, and meeting room.  Audio system control for the lobbies is provided by an AV rack in the gift shop.  Video projection systems are used in the café, gift shop, and education and lecture room, with two projectors in each space.

The security system consists of cameras located throughout the buildings lobbies and hallways.  These are mostly in the first level of the main lobby with a few on the second level and some at the building entrances.  Many of the building’s doors are operated with electronic card swipes.  Some also have audio alarms.

LEED CERTIFICATION:
	This project is seeking LEED certification.

SECTION FOUR | Lighting

For a multi-purpose building such as the August Wilson Center, the lighting design is especially critical.  Various uses place varying demands on the lighting system which the lighting designer must identify in order to produce a successful design.  As a public venue, the lighting is a key for creating a welcoming ambiance and enhancing the overall user experience.

In redesigning four of the primary building spaces (the main Liberty Avenue façade, the first and second level lobbies, the education room and the meeting room), I have focused on using light and luminaires creating a high-class, welcoming appearance while using sophisticated control systems to offer great flexibility for varied uses.  The main motivation for the overall design was the transparency of the façade which creates interaction between all the spaces and likens the building to an open stage.  I have centered my design on creating continuity between spaces with clean layouts and a reduced number of luminaire styles.

In order to provide the flexibility that this building demands, a full building dimming system has been specified.  This system will allow for the integration of photo sensors and occupancy sensors to save energy and utilizes multiple wall stations that can provide preset scenes for each space.  This control system further emphasizes the integration of lighting systems between spaces.

1.  LIBERTY AVENUE FAÇADE

Description:  
The Liberty Avenue façade is approximately 150’ long and two stories (47’) tall, making it appear very horizontal.  It is punctuated by a sail shaped feature on the corner of Liberty Avenue and William Penn Place which forms the focal point of the building’s exterior.  The façade is book ended on the opposite end by a protruding cube that cantilevers out from the plane of the façade by nine feet.  Also at this end of the building is a small seating area outside the café which occupies the corner of Liberty Avenue and Smithfield Street.  The façade sits approximately 25’ back from the street curb.  A row of deciduous trees will run the length of the façade. Spaced approximately 35’ apart, these trees are significant when viewing the façade.  As the façade normal is oriented only a few degrees off of due north, it will almost always been in shadow.

The crux of the liberty avenue façade is its function as a visual opening into the heart of the building.  With clear glass as the predominant material, passersby will have a view into the building day and night.  This condition is particularly relevant to the lighting design.

The relation of the new addition to the Liberty Avenue façade is somewhat limited as the new addition turns the corner onto Smithfield Street.  The new addition does however recess back from the existing façade in parallel planes to further accentuate the volumes of space already developed.

Surface Materials:  
Material descriptions and assumed properties are available in the materials legend, Appendix E, page ##.

This façade is arranged in horizontal bands of clear curtain wall (MATERIAL GLZ-1) and aluminum composite panels (foamed in place) (MATERIAL MTL-3).  Spandrels (MATERIAL GLZ-2) are used where necessary.  The large sail structure is also clad with metal panels and glass but uses fritted glass for the top section (MATERIAL GLZ-5).  It has a black stone base (MATERIAL STN-1).

Irregular façade features are faced with a different but visually similar metal panel system (MATERIAL MTL-1).  Protrusions extending out the top of the building are surfaced in an exposed fastener profiled metal panel system (MATERIAL MTL-2).  The far right section of the facade is faced with a concealed fastener metal panel system (MATERIAL MTL-4).  The sidewalk in front of the building is the standard concrete that is required by the city of Pittsburgh.

Design Criteria:

(Building Exteriors – Prominent Structures)

IESNA Very Important Criteria:
		Appearances of Space and Luminaires
		Light Distribution on Surfaces
		Light Pollution / Trespass
		Point(s) of Interest
		Reflected Glare
		Shadows
		Source/Task/Eye Geometry
		Surface Characteristics
		Category A (3 FC) Vertical Illuminance

IESNA Important Criteria:
			Color Appearance (and Color Contrast)

Direct Glare

Modeling of Faces or Objects

Category B (5 FC) Horizontal Illuminance

	IESNA Somewhat Important Criteria:
		Peripheral Detection
		Sparkle/Desirable Reflected Highlights

ASHRAE/IESNA 90.1 Regulations:

According to table 9.4.5, building facades are allowed 0.2 W/ft2 for each illuminated surface or 5.0 W/linear foot for each illuminated wall.  Also, building entrances and exits are allowed 30W/linear foot of door width (main entrances) or 20 W/linear foot of door width (other doors).  For walkways 10’ wide or greater and plaza areas, an allowance of 0.2 W/ft2 is granted.  Several exceptions are granted by section 9.4.5 but none are applicable to this project.

Pre-Design Criteria Analysis:

This façade is very important and prominent.   Simply washing this service would downplay the dynamic nature of the architecture and do little to create a signature appearance.  Accentuating the sail feature at the end of the façade is a perhaps the most important consideration as it is the keystone of the design.

The placement of luminaires is also a very important consideration.  Improper placement can create harsh glare and can also lead to light pollution.   With taller buildings on adjacent sites, it is important to avoid stray light that may disturb neighbors.  Placing luminaires in a way that does not clutter the clean lines of the architecture will be vital and a significant challenge for the sail feature.

It is very important to consider the overall effect that the lighting will have on the surrounding environment.  Lighting to the appropriate level provides an inviting environment that will encourage visitors to the site.  Lighting the sidewalk to levels that are too high will anger area residents as well as creating a spotlight effect that may make pedestrians uncomfortable.

The small café seating area at the end of the façade also requires special attention.  This area will require adequate levels for eating or conversing with consideration for modeling of faces.  It is also important to create a relaxing environment to encourage patrons to use the space.  This can be done with non-uniform and perimeter lighting.

Design Goals:

- Help to develop the signature nature of the design

- Enhance integration between spaces as a response to the transparency of the façade

- Create focal points to guide patrons and add visual interest

- Define a ‘theatre stage’ theme which allows the building to interact with the streetscape

Design Approach:

- Using the appropriate levels and punctuating the design with accents will help create a signature appearance.  Most importantly, it is necessary to avoid a ‘cheap’ appearance such as a flat wash.

- The interior luminaires will be equally as important to the appearance of the façade as the exterior luminaires.  Placement and consistency throughout the building is paramount.

- The sail feature is a natural focal point which can be accentuated with lighting.  Additionally, pools of light based on proper luminance ratios will guide patrons to the entrances.

- The ‘theatre stage’ can be created using the existing shade system as the metaphorical stage curtain.  The shades can be closed at night and illuminated (approximately 3 fc), giving the façade a closed appearance to contrast the very transparent appearance during normal operating hours.  This will also help reduce light pollution and the related negative consequences.

Luminaire Schedule:

- TYPE A:

(6)  TYPE B:

TOTAL WATTS USED:

POWER DENSITY:

Please see Appendix A for a complete luminaire schedule, light loss factor analysis, and cut sheets.

Lighting Plans:

Please see Appendix B.

Performance Data and Computer Renderings:

Please see Appendices C and D.

Summary Performance Evaluation:

2.  MAIN LOBBY

Description:  
The lobbies, both on the upper and lower levels, act as the main circulation core for the building.  From the main lobby on the first floor, one can reach the permanent exhibit space, theatre, gift shop, box office, and the main grand staircase to the second level.  It totals 4,429 square feet of irregularly shaped space that is defined by surrounding spaces rather than walls.  The lobby runs most of the length of the Liberty Avenue façade, approximately 120’.  An open plenum ceiling exists through much of both the first and second level lobbies

The most notable design element in this space is the large elliptical wall that forms the back of the theater space.  This ‘drum,’ can be seen as a volume from the exterior that protrudes through the first and second levels and out the roof of the structure.

Surface Materials:  
Material descriptions and assumed properties are available in the materials legend, Appendix E, page ##.

The true definition of materials for this space relies heavily on adjacent spaces.  In general, the floor is a finished concrete (MATERIAL CONC-2) while the ceiling is a combination of an open 4' by 4' black grid with 8” metal baffles running perpendicular to the Liberty Avenue facade spaced every 2'.  The baffles hang (MATERIAL XPC-1) at approximately 13'-2” above the finished floor.  Above the grid system is the structure which is covered with black acoustical blanket, as well as mechanical systems which are painted black (MATERIAL PT-2).

The grand staircase, on the south end of the space, is framed by a multi-story stone wall, comprised of three types of stone (MATERIALS STN-1, STN-2, STN-3).  The main walls are painted white (MATERIAL PT-1), which accents are metal (MATERIALS MP-1, MP-2) and wood (MATERIALS WD-1, WD-2).  The north wall is almost entirely curtain wall (MATERIAL GLZ-1).  Shades are not provided for this glazing.  The prominent theater drum is painted green (MATERIAL PT-5) with sections of wood (MATERIAL WD-2).

Furnishings:
No furnishings are currently specified by the architect as they are under a separate contract.  Where applicable, benches have been modeled as seen fit.

Design Criteria:
	(Offices – Lobbies, Lounges, and Reception Areas)

(IESNA Chapter 15)

IESNA Very Important Criteria:
	Appearances of Space and Luminaires

IESNA Important Criteria:
			Color Appearance (and Color Contrast)
			Direct Glare

Light Distribution on Surfaces

Luminances of Room Surfaces

Modeling of Faces or Objects

Surface Characteristics

Category A (3 FC) Vertical Illuminance (at the entrance)

	IESNA Somewhat Important Criteria:
		Daylighting Integration and Control

Flicker (and Strobe)

Reflected Glare

Shadows

Category C (10 FC) Horizontal Illuminance

ASHRAE/IESNA 90.1 Regulations:

According to table 9.6.1 a lobby for a performing arts theater has an LPD (W/ft2) of 3.3.  This is much higher than other types of lobbies which have an LPD of 1.1.  Additionally, section 9.6.3 allows for an additional 1.0 W/ft2 for lighting installed for decorative appearance.

Pre-Design Criteria Analysis:

The IESNA recommendations are accurate in suggesting that the appearance of the space and luminaires is very important for this space.  As the main lobby, everyone will see this space and thus the lighting must accentuate the style of the architecture.

The IESNA Illuminance levels, based on an office lobby, are too low for this space.  Looking at recommendations for theater lobbies, the 20 footcandle level is more appropriate.  Phototropism, or the tendency for humans to be attracted to brighter areas, is certainly important.  Creating points of interest will draw patrons to the center and to the different spaces within the center.

The IENSA also recommends general illuminance levels before and after performances to be 5-15 footcandles.  Therefore, I believe this space needs to be flexible in order to provide proper conditions depending on the function that is occurring at the time.  This space is not only the lobby for the theatre, but also for the galleries, gift shop, bookstore and café.  This all indicates a control system is necessary.

It is important that the lighting in this space creates a relaxed environment to welcome patrons.  Layers of light can be used to create a variety of conditions that may be controlled with a preset system.  A relaxing environment can be created with non-uniform and peripheral lighting.  This mood will be created by highlighting the points of interest within the space.  The ticket booths should be highlighted to drawn the attention of patrons.  Higher illuminances in the gift shop will make it another point of interest.  The entrance to the exhibit spaces should also be highlighted.  The large curved wall that forms the back of the theatre can also be highlighted to create a visual centerpiece for the lobby.

Design Goals:

- Create a relaxing and welcoming environment

- Draw patrons to points of interest

- Flexibility for various uses of the building and of the lobby

- Smooth and appropriate transitions to surrounding spaces

- Energy efficiency

Design Approach:

- Use layers of light that draw focus to perimeter focal points.

- In synergy with design approach one, the perimeter emphasis that creates a relaxing environment will draw patrons to the points of interest.

- The control system will be instrumental to the success of the design.  By utilizing dimming, the space can be illuminated to the desire level based on the current building use.

- A smooth transition can be created by using similar systems throughout the spaces.  This relates to the overall goal of building integration.

- The use of photo sensors integrated with the control system will save energy when ample daylight is available due to the plentiful glazing.  Glare will not be a problem since it is north facing.  It will not be a large increase in cost because dimming is already being used to meet other goals.

Luminaire Schedule:

- TYPE A:

(6)  TYPE B:

TOTAL WATTS USED:

POWER DENSITY:

Please see Appendix A for a complete luminaire schedule, light loss factor analysis, and cut sheets.

Lighting Plans:

Please see Appendix B.

Performance Data and Computer Renderings:

Please see Appendices C and D.

Summary Performance Evaluation:

3.  EDUCATION AND LECTURE ROOM

Description:  
The education and lecture room is an approximately 64’ by 32’ rectangular room located on the north side of the second level.  The main entrance is from the second level lobby through either two standard doors or a large, mechanically operated pivot door.  A second means of egress is provided via a bridge to a separate egress stairwell.  The space is almost completely transparent with large amounts of glazing on all sides.  As all the glass is clear, this transparency exists both looking into the space and looking out of the space.  All of the glass can be covered with mechanically operated black-out shades.

The meeting room is accessed directly from this space, meaning it will partially function as a circulation space.  Access to the meeting room is provided via two glass doors as well as another mechanically operated pivot door.

The south wall features built-in cabinets which break the plane of the glass wall.  These provide storage as well as a kitchen sink.  The room will primarily be used for lectures and presentations.  Retractable presentation screens are available on both the east and west walls.

Surface Materials: 
Material descriptions and assumed properties are available in the materials legend, Appendix E, page ##.
 
North Wall:  The north wall is an exterior wall which is entirely curtain wall (MATERIAL GLZ-1).  A painted gypsum board soffit (MATERIAL PT-1) houses a recessed window shade.  Three structural columns are finished with gypsum board (MATERIAL PT-1) while a beam running the length of the space at approximately 12' above the finished floor is shielded by a formed metal cover.  Radiant heaters are located along the base of this wall.

South Wall:  The south wall is a combination of red/orange painted casework (MATERIAL PT-3) and glazing (MATERIAL GL-1).  The casework surfaces extend approximately 18” into the room, adding depth to the wall.  The glass looks into the grand staircase and onto a stone wall beyond.

West and East Walls: The west and east walls, which are identical, are predominantly a massive, mechanically operated pivot door with a slightly curved wood face (MATERIAL WD-2) and metal trim (MATERIAL MP-2).  A column on either side of the door is finished with gypsum board (MATERIAL PT-1).  Also to either side is a glass passage door in a glass partition wall (MATERIAL GL-2).

Ceiling:  A ceiling grid hangs at 19'-6” above the finished floor.  The grid consists of a 4’ by 4’ black square grid as well as 8” metal baffles spaced 2’ apart that run perpendicular to the Liberty Avenue façade .   The bottom of the structure above is covered in black acoustic blanket.  The ductwork is left exposed and is painted black (MATERIAL PT-2).

Floor:  The floor is carpeted (MATERIAL CPT-1) wall to wall.

Furnishings: 
The room is furnished with stackable chairs that could be removed if necessary.  They are oriented in rows facing the east wall.  A podium is also available.

Design Criteria:

(Educational Facilities – Lecture Halls – Demonstration)

IESNA Very Important Criteria:
	Light Distribution on Task Plane (Uniformity)

Category F (100 FC) Horizontal Illuminance

Category E (50 FC) Vertical Illuminance

IESNA Important Criteria:

Daylighting Integration and Control

Direct Glare

Reflected Glare

Shadows

Source/Task/Eye Geometry

Surface Characteristics

IESNA Somewhat Important Criteria:

Appearances of Space and Luminaires

Color Appearance (and Color Contrast)

Flicker (and Strobe)

Light Distribution on Surfaces

Luminances of Room Surfaces

Modeling of Faces or Objects

Point(s) of Interest

System Control and Flexibility

ASHRAE/IESNA 90.1 Regulations:  
Table 9.6.3 allows for and LPD of 1.4 W/ft2 for classroom / lecture / training rooms.  An additional 1.0 W/ft2 can be used strictly for decorative lighting.

Pre-Design Criteria Analysis:
The IESNA recommendations provide some guidance, but it is necessary to evaluate the individual space in order to make proper decisions.  First, while the illuminance levels recommended for a ‘demonstration’ lecture hall are 100 footcandles horizontal and 50 footcandles vertical, this space is a bit of a hybrid and therefore would best fall into the 30 to 50 footcandles horizontal and 5 to 10 footcandles vertical categories.    These descriptions for these categories are more in line with the true use of the space.

After uniformity, the most critical aspect of the lighting for this space is the integration and control of daylight.  With one entire wall of this space being north facing curtain wall, glare-free daylight is available to reduce electric lighting load.  However, it is also important to consider that this light could be unwanted during a presentation.  Thankfully, black-out shades are specified by the architect.  Daylight harvesting will work hand-in-hand with the dimming flexibility that is required of this space due to the multiple functions it may serve.

Since it is an educational space visual clarity should be achieved.  This will include eliminating or reducing glare and ensuring proper levels for the task plane.  As an upscale space, it is important to consider the appearance of the luminaires.  A ‘clean’ design will also contribute to an impression of visual clarity.  It is important to focus on accurate modeling of faces and objects, but I think it would be good to avoid highlighting points of interest as they may take focus from a presenter.

Keeping with the overall goals, it is very important that this space integrates well with its adjoining spaces, the second level lobby and the meeting room.  A continuity of luminaires from space to space will help maintain a consistent appearance from the exterior as well as maintaining a clean visual appearance inside since the space boundaries are transparent.

Design Goals:

- Create visual clarity

- Provide even and adequate light to the work plane

- Design a flexible system for varied presentations and activities

- Use controls to allow the system to respond to the environment

- Match the existing room aesthetics and compliment the baffle system

Design Approach:

- Utilize a uniform layout of direct luminaires with peripheral emphasis

- Ensure proper levels through numerical verification

- Utilize aimable fixtures and circuit fixtures in proper zones to allow for proper scene control

- Use a dimming system and daylight sensors to maximize energy savings

- Use a thin linear fixture with a modern and stylish appearance

Luminaire Schedule:

(16) TYPE A:  Linear Fluorescent Pendant

(6)   TYPE B:  Linear Fluorescent Wallwash Pendant

(20) TYPE C:  Low Profile Halogen Track Head

TOTAL WATTS USED:

POWER DENSITY:	General: 1.10 W/FT2

Decorative: .73  W/FT2

Please see Appendix A for a complete luminaire schedule, light loss factor analysis, and cut sheets.

Lighting Plans:

Please see Appendix B.

Performance Data and Computer Renderings:

Please see Appendices C and D.

Summary Performance Evaluation:

I believe this design satisfies all the goals while also meeting code regulations for power density.  The goals for the design, the room geometry, and the ceiling system greatly limit the available luminaires which can be used.  By using a combination of track and direct fixture that are combined into one system, I believe the lighting is flexible enough to allow the space to be used for a variety of applications including teaching, speaking, displays and gathering.

Calculations show that the downlights alone provide an average of 41 footcandles to the space.  This would be adequate for a typical classroom setting.  Furthermore, with a large amount of north-facing glazing, glare-free daylight will be readily available.  For accenting a speaker or accenting display tables, the track fixtures will provide additional light.

The key to this system is that it integrates with the rest of the lobby, both on the second floor and below on the first floor.  This will help achieve the desired goals for the visual appearance of the building from the exterior.

4.  MEETING ROOM

Description:  
The meeting room is prominently situated within the sail on the second level and in the northeast corner of the building.  The room is approximately 24' by 32' and is accessed from the education and lecture room by standard doors or a large mechanical pivot door.  Because it is in the sail the east wall is arched (in section view).  Large sections of curtain wall exist on the south, east, and north sides of the space which will provide plenty of daylight.  Shading is provided for all of the glazing.  The ceiling slopes, opening to the curved wall of the sail.  While the meeting room label is ambiguous, the primary function of the space would be to host donors or hold other small, private events.

Surface Materials:  
Material descriptions and assumed properties are available in the materials legend, Appendix E, page ##.

North and South Walls:  Mirror images of each other, the north and south walls are half curtain wall (MATERIAL GLZ-1) and half painted gypsum (MATERIAL PT-1).  There is a column at approximately the third point of the walls at which the ceiling begins to slope upwards towards the sail.

East Wall:  The east wall curves as it is a portion of the sail that forms the corner of the building.  Curved curtain wall (MATERIAL GLZ-3) forms the center of this wall while the left and right sides are painted gypsum (MATERIAL PT-1).

West Wall:   The west wall is the same as the East and West walls of the education and lecture room.

Ceiling:  The ceiling in this space is painted gypsum (MATERIAL PT-1).  Moving from west to east, it is level before beginning to slope at column line A1.  This creates an aperture effect opening the view looking out of the sail.

Floor:  This space is fully carpeted (MATERIAL CPT-1).

Furnishings:  
Furnishings for this space are not provided on the drawings.  It is assumed that the furniture would include somewhat informal seating arrangements.

Design Criteria:

(Conference Rooms – Meeting)

IESNA Very Important Criteria:
		Appearance of Space and Luminaires
		Direct Glare
		Modeling of Faces and Objects

IESNA Important Criteria:
			Color Appearance (and Color Contrast)
			Light Distribution on Surfaces
			Light Distribution on Task Plane (Uniformity)
			Luminances of Room Surface
			Reflected Glare
			Surface Characteristics
			Illuminance Category D (30 FC) Horizontal
			Illuminance Category B (5 FC) Veritcal

IESNA Somewhat Important Criteria:
			Daylighting Integration and Control
			Flicker (and Strobe)
			Shadows
			Source/Task/Eye Geometry

ASHRAE/IESNA 90.1 Regulations: 
Table 9.6.3 allows for and LPD of 1.3 W/ft2 for conference / meeting / multipurpose spaces.  An additional 1.0 W/ft2 can be used strictly for decorative lighting.

Pre-Design Criteria Analysis:
The meeting room’s location within the building makes it one of the most dynamic and interesting spaces.  Sitting within the sail, it will receive a lot of daylight, making integration and control of daylight an extremely important issue.  However, it is also important to consider how this is controlled, because the view from this space should also be considered.  One of the other important factors is the flexibility of the chosen lighting system.  The nebulous nature of the space means the lighting may have to respond to a wide variety of uses.  A preset control system will likely be beneficial for this space.

The appearance of the luminaires will also be important as they could possibly be a decorative element for the space.  This would also allow for an additional w/sf allowance according to the ASHRAE 90.1 Standard.  It is important to create a high class appearance in this space.  The suggested Illuminance levels seem accurate for this space, but again, flexibility is essential.

As previously stated, this space must show some continuity with the education room, as they are separated by a glass partition.  The contribution of the interior lighting system of this space will have a great impact on the exterior appearance of the building.

Design Goals:

- Create a warm and relaxing ambiance

- Design for an upscale appearance

- Provide strong facial rendering

- Help make the space a signature room

Design Approach:

- Utilize non-uniformity, peripheral emphasis, and low color temperature sources

- Use decorative luminaires to provide a distinct style

- Avoid direct overhead downlight

- Use decorative, stylish luminaires with a modern appearance

Luminaire Schedule:

(10) TYPE D: Gimbal Recessed Spotlight – 90W

(5)   TYPE E:  Gimbal Recessed Spotlight – 50W

(6)   TYPE F:  Two Cell Rectangular Recessed Downlight

(12) TYPE G: Linear Indirect Pendant

TOTAL WATTS USED:

POWER DENSITY: 	General: 1.33 W/FT2

Decorative: .88  W/FT2

Please see Appendix A for a complete luminaire schedule, light loss factor analysis, and cut sheets.

Lighting Plans:

Please see Appendix B.

Performance Data and Computer Renderings:

Please see Appendices C and D.

Summary Performance Evaluation:

This space is difficult to light because it is a small space with a high and sloped ceiling.  Its location in the ‘sail’ means fixture selection is extremely critical because they are visible from the street.  The nebulous nature of this space also makes lighting for a specific activity rather difficult.

The downlights highlight materials and the unique volumes of the space while the overhead indirect pendants light the ceiling, providing a bright surface that is visible from the exterior.  The design provides an average of approximately 20 footcandles, which will be much greater in the day when daylight is available.  This light is focused around the perimeter of the space.  These levels should be adequate for creating a warm and welcoming space for gathering.

SECTION FIVE | Electrical

1A. MAIN LOBBY and LIBERTY AVENUE FACADE

[with SECOND LEVEL LOBBY, GIFT SHOP, BOX OFFICE, GRAND STAIRCASE]

Existing Design

The existing electrical design for the main lobby utilizes three separate lighting panels (1N1, 1E1, ALDR5).  These panels are in various locations and control is split between dimming and switching.  The other spaces that will be combined with the main lobby for the redesigned control system also use the three previously mentioned panels, as well as 2N1 and 2E1.

Redesigned System

The new electrical system for the lower and upper lobbies as well as connected spaces will combine many lighting loads onto a single dimming system.  More dimming control was a desire for the redesigned lighting system and therefore it was a logical choice to combine these loads into a complete system, rather than using a collection of panels to supply power.

A new dimming rack has been specified that is large enough to handle all the aforementioned loads.  It also eliminates the need for separation of loads onto normal and emergency circuits due to an automatic emergency transfer switch located in the dimmer rack assembly.  The panel specified for these spaces has seven modules with four control circuits per module with a maximum of 20A connected load per circuit.  The panel is main lugs only and is protected at the distribution panel.

The new system utilizes 23 circuits with a total of 24.89 KW of connected load and has six circuits of spare capacity.  A total demand load of 86.43 A was used to size the feeder and protection.   The feeder has been sized at (4) #3.  The breaker protected the feeder on distribution panel 1NDP1 is still sized at 100 A.

The 23 circuits are divided into 16 control zones.  Since these loads comprise all the public spaces of the building, they will be controlled by a single head unit located in the box office.

Dimmer rack/panelboard layouts for both the existing and new system are provided below. See Appendix F and G for full size worksheets and schedules.  Electrical plans are available in Appendix H.  Product Information for the dimmer racks is available in Appendix K.

Redesign Analysis

The redesigned system offers incredible flexibility and greatly simplifies the existing system.  Utilizing a main point of control will provide management with the ability to set and alter various scenes on the fly, creating a dynamic environment.  Electrically, the system is convenient and centralized.  The lighting loads are grouped together and are separated from the auditorium dimmer racks.

Figure 5.1A.1 | Existing Dimmer Rack DR-201

Figure 5.1A.2 | Existing Panel 2N1

Figure 5.1A.3 | Existing Panel 1N1

Figure 5.1A.4 | Existing Panel 2E1

Figure 5.1A.5 | Existing Panel 1E1

Figure 5.1A.6 | New Dimmer Rack DR101/201

1B. EDUCATION AND LECTURE ROOM and MEETING ROOM

Existing Design

The current design for the education and lecture room uses a dimmer rack (DR202) connected to a distribution panel (1N1).  DR202 serves only the education and lecture room and the meeting room.   In total between the two rooms, 5 circuits are used.  The total connected load was 5.13 KW, which was protected by a 100A three pole circuit breaker on panel 1NDP1.  This system was controlled by a main control panel in room 202 with two satellite control panels, one in each space.  An emergency dimmer transfer rack is used to provide emergency power to the rack.

Redesigned System

The new system for the education and lecture room will utilize the same organization as the previous system.  The lighting design is not extremely different and the load is nearly identical.  There are new fixtures and different zones, but the total load is still very small.  A new dimming rack system has been specified that eliminates the need for a second emergency transfer panel.  The panel specified for these spaces has four modules with four control circuits per module with a maximum of 20A connected load per circuit.  The panel is main lugs only and is protected at the distribution panel.

The new system utilizes 8 circuits with a total of 5.04 KW of connected load and has eight circuits of spare capacity.  A total demand load of 27A was used to size the feeder and protection.   The feeder has been sized at (4) #10.  The breaker protected the feeder on distribution panel 1NDP1 is still sized at 30A.

The system will be controlled by two main wall panels, one in the Meeting Room and one in the Education Room.  The education will also feature a secondary wall dimmer switch.  These panels will control both the lights and the window shades that are present in both rooms.  Photosensors will be added to the Education Room to dim the exterior zones because daylight analysis shows that ample daylight is available in the space.

Dimmer rack/panelboard layouts for both the existing and new system are provided below. See Appendix F and G for full size worksheets and schedules.  Electrical plans are available in Appendix H.  Product Information for the dimmer racks is available in Appendix K.

Redesign Analysis

The new system does not differ dramatically from the existing system, but the system is simplified slightly by eliminating an external emergency power transfer rack.  The streamlined control system will allow for control of both lighting and shading devices.  Extra room is left should the need to expand the system arise.

Figure 5.1B.1 | Existing Dimmer Rack DR-202/207

Figure 5.1B.2 | New Dimmer Rack DR-202/207

2.  PHOTOVOLTAIC ARRAY ANALYSIS

With the growth of the LEED movement, photovoltaic (PV) systems are surging as a popular ‘green’ choice for owners who want an energy conscious design.  With numerous governmental incentives available, the cost-effectiveness of implementing such a system can become complex.  As a building seeking LEED certification, a PV system is something that should at least be considered by the designer.

This analysis was conducted utilizing RETScreen , an analysis tool for energy design.  Since enough area is not available to provide power for the entire building, the system needs to be an on-grid system.  The designed system would not use a battery supply and excess energy would be transferred back to the grid.  The following is a summary of the analysis:

Roof Area available for PV array: Approximately 12,000 ft2 (1115 m2)

Product: BP Solar 5170S

Power Produced: 192KWh

Physical Size: 1.26 m2

Efficiency: 13.5%

Total System Efficiency:	  3%

Unit Cost: $5,750

Maintenance Costs:  $10,000/10 Years

Design Costs: $15,000

Other Equipment Costs: $100,000

Figure 5.2.1 | Available Area for PV Array

Annual Energy Available (Pittsburgh): 1.53MWh/m2

Energy Rate: .1236 cents/KWh

Energy Savings/Year/Panel: $28

Financial Incentives:

- Federal tax incentives do not apply since the August Wilson Center is a non-profit organization.

- The Pennsylvania Energy Harvest Grant, or any other state incentive, is no longer available.

- Duquesne Light does not currently offer any incentives for implementation of renewable energy.

Payback Period:  This installation will never provide a return on the investment.

Figure 5.2.2 | PV Solar Radiation Map

Photovoltaic Array Feasibility Conclusion:

Based on the calculations, it is certainly not feasible to use a photovoltaic array for this project.  Figure 5.2.2 shows that Pittsburgh does not receive a substantial amount of solar energy.  Another factor affecting the feasibility is the low utility rate that this property receives.  Based on the buildings location in the urban center of Pittsburgh and the shadowing provided by adjacent buildings, the actual energy savings would likely be less that the model predicts.  Finally, since the August Wilson Center is a non-profit organization, it cannot receive federal and state tax incentives for solar energy.  This places the full cost of the initial installation on the owner, significantly affecting the payback of the system.

3.  SYSTEM TYPE CONVERSION STUDY

The existing design for the August Wilson Center utilizes two parallel service entrances, providing redundancy should one fail through a collector bus which connects to two main switchboards.  One of the switchboards (MSB1) feeds primarily mechanical loads and the emergency power system while the second switchboard (MSB2) feeds predominantly lighting and receptacle loads.  Both switchboards are currently designed at 280Y/120V.

Studying the single line diagram revealed that MSB1 could be switched to a 480/277V system with minimal disruption to the system.  One drawback to this change is the elimination of the point of redundancy, however.   In order to make a justifiable decision on the advantage of the system conversion, a comparative cost analysis was conducted.

The Existing System:
The portion of the existing system being studied includes the following equipment:

| Table 5.3.1: Existing Design Equipment Schedule |
| --- |
| TYPE | TAG | LOCATION | DESCRIPTION |
| Transformer | NA | Transformer Vault | Duquesne Light Transformer |
| Main Switchboard | MSB1 | Basement (013) | 208Y/120, 3000A MCB |
| Distribution Panel | BNDP1 | Basement (013) | 208Y/120, 1200A MLO |
| Distribution Panel | BNDP2 | Basement (013) | 208Y/120, 400A MLO |
| Branch Circuit Panel | 2P1 | Electrical Room (212) | 208Y/120, 225A MLO |
| Branch Circuit Panel | 1KN1 | Kitchen (140) | 208Y/120, 400A MLO |
| Branch Circuit Panel | 1KN2 | Kitchen (140) | 208Y/120, 225A MLO |

A portion of the existing single line diagram as well as the panelboards that will change are shown on the following pages.  Full size images are available in Appendices F-J.

Figure 5.3.1 | Existing System to be redesigned.

Figure 5.3.2 | BNDP1 


Figure 5.3.3 | BNDP2

Figure 5.3.4 | 1KN1

Figure 5.3.5 | 1KN2

Figure 5.3.6 | 2P1

The Redesigned System:
Redesigning the system involved recalculating the loading on each panelboard in order to resize the bus and the feeder.  Also, the addition of two transformers is necessary to accommodate loads that must run at 120V.  Below is the new equipment schedule and panelboard schedules.  A new single line diagram and full size images of the panelboard schedules are available in Appendices F-J.

| Table 5.3.2: Redesign Equipment Schedule |
| --- |
| TYPE | TAG | LOCATION | DESCRIPTION |
| Transformer | NA | Trans. Vault | Duquesne Light Transformer (Unch) |
| Transformer | 2T1 | Electrical Room (212) | 9 KVA, 480V to 108Y/120V |
| Transformer | 1T3 | Kitchen (140) | 30 KVA, 480V to 108Y/120V |
| Main Switchboard | MSB1 | Basement (013) | 480/277, 1600A MCB |
| Distribution Panel | BNDP1 | Basement (013) | 480/277, 400A MLO |
| Distribution Panel | BNDP2 | Basement (013) | 480/277, 100A MLO |
| Branch Circuit Panel | 2P1 | Electrical Room (212) | 480/277, 100A MLO |
| Branch Circuit Panel | 2P1A | Electrical Room (212) | 480/277, 60A MLO |
| Branch Circuit Panel | 1KN1 | Kitchen (140) | 208Y/120, 400A MCB |
| Branch Circuit Panel | 1KN2 | Kitchen (140) | 208Y/120, 225A MLO (Unchanged) |

Figure 5.3.7 | New Panel BNDP1

Figure 5.3.8 | New Panel BNDP2

Figure 5.3.9 | New Panel 2P1

Figure 5.3.10 | New Panel 2P1A

Sample Calculations for New Sizing:

Brach Circuit Breaker for Motor (Sample for Elevator No. 2):  
MCA (NEC 2005 430.250) = 65A * 1.25 (First Motor) = 81.25A

MOPD (NEC 2005 430.52) = 250% (Inverse Time Breaker)

2.5 * 65A = 162.5A

BREAKER SIZE: 150A

WIRE SIZE: (3) #4 Conductors

Transformer (Sample for Panel 1KN1):

Calculated Design Load = 23.3 KW

Transformer = 30 kVA

Secondary Protection = 110A (125A)

Primary Protection = 30.1A (50A)

Cost Analysis:

The cost comparison between the new and existing systems was completed using R.S. Means 2008 Electrical Cost Data.  The existing system from the most current recent set of drawings is designed and sized for the original contract, which was a guaranteed maximum price (GMP).  Because of this, all equipment and feeders were grossly oversized.  Feeders were sized to match bus size.  In order for the cost estimate to provide comparable results, this same method was utilized.  The bus sizes have all been resized based on the new panel demand loads, however, greatly reducing the feeder sizes.  The cost comparison is broken down in the following table:

System Conversion Conclusion:
As shown in Table 5.3.3, converting MSB1 and its connected loads to a 480/277V system saves a significant amount of money.  For a project that is trying to reduce the bottom line, this change seems to be a viable option.  The tabulated data does not include further cost savings that would result from a reduction of individual breakers for branch circuits.

The second factor that must be considered in the conversion of this system is the loss of redundancy provided by the collector bus.  Since the system includes a substantial emergency generator and the system does not include critical loads, it is my opinion that using a 480/277V system for switchboard MSB1 is an appropriate choice for this project.

4.  PROTECTIVE DEVICE COORDINATION STUDY and FAULT CURRENT ANALYSIS

As a sample calculation, a protective device coordination study and a fault current analysis was performed for a selected path through the system.  The calculations that follow summarize these two procedures.  That path is as follows:

Utility Transformer > Main Switchboard (MSB1) > Distribution Panel (1NDP1) > End-Use Panel (1N1)

The results show that the currently designed system uses has equipment specified which is, in one cases, is less than that required by the calculations.  Branch circuit panelboard 1TN1 requires 25000 AIC but the specified equipment is rated at 22,000 AIC.

Figure 5.4.1 | Protective Device Coordination

SECTION SIX | Architecture

SECTION SEVEN | Acoustics

Acoustics is an important but often overlooked element of architectural design.  In certain cases, a poor acoustical design can ruin an otherwise well-designed space.  For the August Wilson Center, acoustics is certainly paramount.  As a center for arts and culture, the center will be home to a variety of acoustical situations from spoken word performances to small recitals to lectures to full theatrical performances.   For this analysis, two of the critical spaces were selected, analyzed, and if necessary, redesigned.  Detailed calculations of reverberation time and sound transmission coefficients were used to draw conclusions about the acoustical effectiveness of the designs.

1.  THE MUSIC CAFÉ
The Music Café is characterized by Perkins + Will as follows:

The café is located at sidewalk level, accessible directly from the street and from within the center. It will function as a traditional museum café and sidewalk café during the day. A seating terrace is located outside and adjacent to the café. Wired for internet access and designed to accommodate a wide range of emerging technologies, the Café provides an electronic link to visitors worldwide.

Modeled after New York’s BAM café or Joe’s Pub the Café is also designed to accommodate an on-going menu of programs and to function as an alternative performance space for intimate performances with limited seating for jazz, spoken word, poetry and other new performance forms in a club setting at night. A portable stage and theatrical lighting will be imported to support such performances as required.

This space is essential a large rectangular box with three sides glass, a hard, sound reflecting material.  The existing design does recognize the need for acoustical design elements, utilizing hanging metal baffles and acoustical blanket over 80% of the underside of the floor structure above.

Based on the use description provided by the architect, a reverberation time of approximately 1.0 to 1.2 seconds would be ideal.  This would place the space somewhere between speech and speech/music use.  According to the Architectural Acoustics: Principles and Design a very high STC value (60+) between the Music Café and Lobby would be ideal.  This is important to both spaces, as a spoken word performance in the café could suffer if a large crowd was gathering in the lobby for a performance in the main theater, while the lobby must remain quiet during a performance in the main theater if patrons are entering or exiting the auditorium since a main set of doors is directly across from the Music Café.

Figure 7.1.1 | Music Café Reflected Ceiling Plan

2.  MULTI-PURPOSE ROOM
The multi-purpose room is characterized by Perkins + Will as follows:

Located at the second level, the multipurpose room functions as a flexible performance space and with its sprung hardwood floors also serves as the Center’s rehearsal hall. It will be available for programming of special events including dance parties and social events such as weddings, fundraisers, birthday parties and other celebrations. Theatrical lighting and sound systems, portable stage and portable practice bar can be imported as required per activity requirements. The room benefits from significant daylighting due to large areas of north facing windows overlooking Liberty Avenue and can also be fully darkened.

Based on the description from Perkins + Will, this will be a very dynamic space with a variety of uses.  This makes acoustical design more complex.  A reverberation time of 1.0 to 1.2 seconds would satisfy the majority of uses for this space.

SECTION EIGHT | Summary and Conclusions

SECTION NINE | References

http://www.dsireusa.org

Acoustics book

Wikipedia

Retscreen

IES Handbook

NEC 2005

Software: AGI-32, Autodesk VIZ 2008, Autodesk AutoCAD 2008, Adobe Photoshop CS3

SECTION TEN | Acknowledgements

# Text boxes

2

3

4
5

6
6
6
6
7

8
9
9
9

10
11
11
11
11

12
12
12

23

3

4

A1
B1
C1
D1
E1
F1
G1
H1
I1
J1
K1
L1