## Slide 1
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
senior thesis presentation

## Slide 2
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
introduction
senior thesis presentation
UNLV Greenspun Hall
Las Vegas, Nevada

## Slide 3
introduction
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
project history
UNLV Greenspun Hall
Las Vegas, Nevada
Officially dedicated on December 2, 2008
Classrooms and offices
LEED Gold Certification
Two buildings sharing a central courtyard and basement
Design Objectives: Innovation and efficient design
represents a commitment and investment for the future through its sustainable design and architecture

## Slide 4
project history
existing systems
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
3 dedicated outdoor air AHU’s, 5 total
Chilled Beam distribution
(2) Carrier 19XR Centrifugal Chillers
(2) Marley Open Cell Cooling Towers
Basic Heat Rejection Loop and Load Loop
Mechanical System
System Description

## Slide 5
Introduction
Project History
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
existing systems
Structural
Concrete structure
Steel framing supports photovoltaic array
Foundation – spread and strip footers
Roof – Non composite deck on 7’ joist spacing
Electrical
Photovoltaic array – 50,000 KWh’s/year
Lighting – 1.1 watts/ft2
3 distribution panels – total = 2,200 amps
Other Systems
Existing Systems

## Slide 6
existing systems
improving the system
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
3 Alternatives
(1) Replace existing chillers w/ absorption chillers
Solar absorber array to drive generators
(2) Add chilled water storage to Alternative 1
(3) Add chilled water storage to existing system
Goal:
make a LEED Gold building better

## Slide 7
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
improving the system
Load profiles taken from TRACE 700 calc
Simplify the calculation
  Every month has a typical day
  Every typical day has a load profile and TMY data
Used to calculate existing system (control) and alternative’s annual regulated energy costs
Procedure

## Slide 8
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Convert Load Profiles to KW’s using chiller η
  0.837 KW/ton
Use consumption and demand charges to calculate annual cost ~ $35,000
Control
Electric Charge |  | Summer | All Other Periods
 | On-Peak | $0.10001 | $0.06406
Consumption | Mid-Peak | $0.0865 | 
 | Off-Peak | $0.06230 | 
 | On-Peak | $9.17 | $0.50
Demand | Mid-Peak | $0.68 | 
 | Off-Peak | $0.00 | 
 | Cooling Load (tons) vs. Hour/day |  |  |  |  |  |  |  |  |  |  | 
 | J | F | M | A | M | J | J | A | S | O | N | D
0:01 - 1:00 | 0 | 0 | 0 | 0 | 0 | 17.39 | 17.91 | 19.33 | 15.93 | 0 | 0 | 0
1:01 - 2:00 | 0 | 0 | 0 | 0 | 0 | 10.87 | 11.2 | 12.08 | 9.96 | 0 | 0 | 0
2:01 - 3:00 | 0 | 0 | 0 | 0 | 0 | 10.87 | 11.2 | 12.08 | 9.96 | 0 | 0 | 0
3:01 - 4:00 | 0 | 0 | 0 | 0 | 0 | 10.87 | 11.2 | 12.08 | 9.96 | 0 | 0 | 0
4:01 - 5:00 | 0 | 0 | 0 | 0 | 0 | 8.69 | 8.96 | 9.66 | 7.97 | 0 | 0 | 0
5:01 - 6:00 | 0 | 0 | 0 | 0 | 0 | 8.69 | 8.96 | 9.66 | 7.97 | 0 | 0 | 0
6:01 - 7:00 | 0 | 0 | 0 | 0 | 0 | 15.22 | 15.67 | 16.91 | 13.94 | 0 | 0 | 0
7:01 - 8:00 | 6.62 | 5.99 | 6.37 | 5.62 | 6.39 | 23.91 | 24.63 | 26.57 | 21.91 | 6.7 | 6.18 | 6.29
8:01 - 9:00 | 8.43 | 7.62 | 8.11 | 7.16 | 8.13 | 30.43 | 31.35 | 33.82 | 27.88 | 8.53 | 7.87 | 8.01
9:01 - 10:00 | 38.52 | 34.85 | 37.07 | 32.72 | 37.19 | 139.11 | 143.31 | 154.6 | 127.45 | 38.97 | 35.98 | 36.61
10:01 - 11:00 | 51.16 | 46.28 | 49.23 | 43.46 | 49.39 | 184.76 | 190.33 | 205.33 | 169.27 | 51.76 | 47.79 | 48.62
11:01 - 12:00 | 52.37 | 47.37 | 50.39 | 44.48 | 50.55 | 189.11 | 194.81 | 210.16 | 173.26 | 52.98 | 48.91 | 49.77
12:01 - 13:00 | 54.17 | 49 | 52.13 | 46.02 | 52.3 | 195.63 | 201.53 | 217.41 | 179.23 | 54.8 | 50.6 | 51.48
13:01 - 14:00 | 58.39 | 52.81 | 56.18 | 49.59 | 56.36 | 210.84 | 217.2 | 234.32 | 193.17 | 59.07 | 54.53 | 55.49
14:01 - 15:00 | 60.19 | 54.45 | 57.92 | 51.13 | 58.11 | 217.37 | 223.92 | 241.57 | 199.14 | 60.89 | 56.22 | 57.2
15:01 - 16:00 | 60.19 | 54.45 | 57.92 | 51.13 | 58.11 | 217.37 | 223.92 | 241.57 | 199.14 | 60.89 | 56.22 | 57.2
16:01 - 17:00 | 56.58 | 51.18 | 54.44 | 48.06 | 54.62 | 204.32 | 210.49 | 227.07 | 187.2 | 57.24 | 52.85 | 53.77
17:01 - 18:00 | 53.57 | 48.46 | 51.55 | 45.5 | 51.71 | 193.46 | 199.29 | 214.99 | 177.24 | 54.2 | 50.04 | 50.91
18:01 - 19:00 | 34.31 | 31.03 | 33.01 | 29.14 | 33.12 | 123.9 | 127.64 | 137.69 | 113.51 | 34.71 | 32.05 | 32.61
19:01 - 20:00 | 16.25 | 14.7 | 15.64 | 13.8 | 15.69 | 58.69 | 60.46 | 65.22 | 53.77 | 16.44 | 15.18 | 15.44
20:01 - 21:00 | 13.84 | 12.52 | 13.32 | 11.76 | 13.36 | 49.99 | 51.5 | 55.56 | 45.8 | 14.01 | 12.93 | 13.16
21:01 - 22:00 | 11.44 | 10.34 | 11 | 9.71 | 11.04 | 41.3 | 42.55 | 45.9 | 37.84 | 11.57 | 10.68 | 10.87
22:01 - 23:00 | 10.23 | 9.26 | 9.85 | 8.69 | 9.88 | 36.95 | 38.07 | 41.07 | 33.85 | 10.35 | 9.56 | 9.72
23:01 - 24:00 | 0 | 0 | 0 | 0 | 0 | 26.08 | 26.87 | 28.99 | 23.9 | 0 | 0 | 0

## Slide 9
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
(2) Single Effect Absorption Chillers
Solar absorber array
(2) Back-up Boilers
Alternative 1

## Slide 10
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 1
Solar absorber array can sufficiently maintain the hot water temperature needed to drive the generators
425 absorbers = 17,000 ft2
Boilers only needed when the sun isn’t shining
System consumes natural gas instead of electricity
Average Hourly Statistics for Direct Normal Solar Radiation Wh/m² |  |  |  |  |  |  |  |  |  |  |  | 
Hour | J | F | M | A | M | J | J | A | S | O | N | D
0:01 - 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1:01 - 2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2:01 - 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3:01 - 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4:01 - 5:00 | 0 | 0 | 0 | 1 | 42 | 69 | 42 | 2 | 0 | 0 | 0 | 0
5:01 - 6:00 | 0 | 0 | 16 | 185 | 340 | 429 | 347 | 253 | 90 | 23 | 0 | 0
6:01 - 7:00 | 0 | 68 | 244 | 501 | 535 | 640 | 605 | 551 | 452 | 381 | 161 | 27
7:01 - 8:00 | 302 | 348 | 457 | 674 | 687 | 736 | 726 | 701 | 644 | 646 | 481 | 371
8:01 - 9:00 | 510 | 523 | 545 | 720 | 777 | 784 | 755 | 780 | 695 | 730 | 607 | 549
9:01 - 10:00 | 588 | 606 | 593 | 770 | 798 | 752 | 797 | 807 | 798 | 767 | 689 | 613
10:01 - 11:00 | 655 | 679 | 588 | 769 | 761 | 791 | 810 | 815 | 833 | 748 | 697 | 687
11:01 - 12:00 | 642 | 630 | 615 | 766 | 679 | 760 | 820 | 812 | 817 | 780 | 735 | 676
12:01 - 13:00 | 598 | 662 | 641 | 714 | 689 | 770 | 802 | 752 | 817 | 756 | 724 | 675
13:01 - 14:00 | 577 | 620 | 578 | 673 | 718 | 759 | 775 | 682 | 752 | 696 | 696 | 658
14:01 - 15:00 | 564 | 543 | 554 | 649 | 690 | 703 | 756 | 658 | 641 | 675 | 629 | 602
15:01 - 16:00 | 476 | 443 | 429 | 607 | 658 | 698 | 686 | 585 | 604 | 596 | 463 | 406
16:01 - 17:00 | 144 | 265 | 314 | 470 | 585 | 606 | 614 | 534 | 441 | 323 | 117 | 44
17:01 - 18:00 | 0 | 15 | 108 | 266 | 352 | 435 | 494 | 369 | 160 | 13 | 0 | 0
18:01 - 19:00 | 0 | 0 | 0 | 17 | 46 | 152 | 182 | 53 | 0 | 0 | 0 | 0
19:01 - 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20:01 - 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21:01 - 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22:01 - 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23:01 - 24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 11
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 1
Annual Regulated Energy Cost
Chiller Output
Boiler Input
Generator Input = Boiler Output
Gas Firing Rate (CHF) of Boiler vs. Hour/day |  |  |  |  |  |  |  |  |  |  |  | 
Hour | J | F | M | A | M | J | J | A | S | O | N | D
0:01 - 1:00 | 0 | 0 | 0 | 0 | 0 | 376.04 | 387.38 | 417.91 | 344.52 | 0 | 0 | 0
1:01 - 2:00 | 0 | 0 | 0 | 0 | 0 | 235.03 | 242.12 | 261.19 | 215.32 | 0 | 0 | 0
2:01 - 3:00 | 0 | 0 | 0 | 0 | 0 | 235.03 | 242.12 | 261.19 | 215.32 | 0 | 0 | 0
3:01 - 4:00 | 0 | 0 | 0 | 0 | 0 | 235.03 | 242.12 | 261.19 | 215.32 | 0 | 0 | 0
4:01 - 5:00 | 0 | 0 | 0 | 0 | 0 | 188.02 | 193.69 | 208.96 | 172.26 | 0 | 0 | 0
5:01 - 6:00 | 0 | 0 | 0 | 0 | 0 | 188.02 | 193.69 | 208.96 | 172.26 | 0 | 0 | 0
6:01 - 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.96 | 0 | 0 | 0
7:01 - 8:00 | 143.18 | 129.51 | 105.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.71 | 136.07
8:01 - 9:00 | 21.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9:01 - 10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10:01 - 11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11:01 - 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12:01 - 13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13:01 - 14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14:01 - 15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15:01 - 16:00 | 690.7 | 1116.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842.53 | 1237.01
16:01 - 17:00 | 1223.57 | 1106.75 | 1177.35 | 629.02 | 0 | 0 | 0 | 0 | 3942.67 | 1237.82 | 1142.84 | 1162.79
17:01 - 18:00 | 1158.49 | 1047.88 | 1114.73 | 984.04 | 1118.33 | 4183.47 | 4309.66 | 4649.26 | 3832.77 | 1171.98 | 1082.05 | 1100.94
18:01 - 19:00 | 741.95 | 671.11 | 713.93 | 630.23 | 716.24 | 2679.3 | 2760.12 | 2977.62 | 2454.7 | 750.59 | 693 | 705.1
19:01 - 20:00 | 351.45 | 317.9 | 338.18 | 298.53 | 339.27 | 1269.14 | 1307.42 | 1410.45 | 1162.75 | 355.54 | 328.26 | 333.99
20:01 - 21:00 | 299.38 | 270.8 | 288.08 | 254.3 | 289.01 | 1081.12 | 1113.73 | 1201.49 | 990.49 | 302.87 | 279.63 | 284.51
21:01 - 22:00 | 247.32 | 223.7 | 237.98 | 210.08 | 238.75 | 893.1 | 920.04 | 992.54 | 818.23 | 250.2 | 231 | 235.03
22:01 - 23:00 | 221.28 | 200.16 | 212.93 | 187.96 | 213.61 | 799.09 | 823.19 | 888.06 | 732.1 | 223.86 | 206.68 | 210.29
23:01 - 24:00 | 0 | 0 | 0 | 0 | 0 | 564.06 | 581.08 | 626.87 | 516.78 | 0 | 0 | 0
ηchiller
ηboiler

## Slide 12
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 1
Regulated Energy Cost
Additional Pumping Cost
Total Annual Operating Cost
Natural Gas Cost Analysis |  |  |  |  |  |  |  |  |  |  |  | 
Month | J | F | M | A | M | J | J | A | S | O | N | D
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Therm/day | 5.1 | 5.08 | 4.19 | 3.19 | 2.92 | 12.9 | 13.3 | 14.37 | 16.04 | 4.29 | 4.87 | 5.41
Therm/month | 158.07 | 142.35 | 130 | 95.8 | 90.4 | 388 | 413 | 445.34 | 481.09 | 133.08 | 146 | 168
Cost/Therm | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
Cost/Month | 155.41 | 139.96 | 128 | 94.2 | 88.9 | 381 | 406 | 437.84 | 472.99 | 130.84 | 144 | 165
Base/Month | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Total/Month | 185.41 | 169.96 | 158 | 124 | 119 | 411 | 436 | 467.84 | 502.99 | 160.84 | 174 | 195
Total | 3103.24 |  |  |  |  |  |  |  |  |  |  | 
Existing Pump Cost | 8265.62 |  |  |  |  |  |  |  |  |  |  | 
Additional Pump Cost | 3760 |  |  |  |  |  |  |  |  |  |  | 
Total System Cost | $15,128.86 |  |  |  |  |  |  |  |  |  |  | 
$11,370
$3,760
$15,130

## Slide 13
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 2
(2) Single Effect Absorption Chillers
Solar absorber array
(2) Back-up Boilers
Chilled Water Storage

## Slide 14
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Sizing Strategy: assist absorber array during peak loading to reduce the volume of the array
Not economical to utilize thermal storage for non-peak months
900 ton tank, direct interface
~76,000 gallons
Reduced Solar Array
290 absorbers
Eliminates 135 absorbers and 5,400 ft2 of roof space
Alternative 2

## Slide 15
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 2
Charging and Discharging
Cooling Load (tons) vs. Hour/day |  |  |  | 
Hour | J | J | A | S
0:01 - 1:00 | 17.39 | 17.91 | 19.33 | 15.93
1:01 - 2:00 | 10.87 | 11.2 | 12.08 | 9.96
2:01 - 3:00 | 10.87 | 11.2 | 12.08 | 9.96
3:01 - 4:00 | 10.87 | 11.2 | 12.08 | 9.96
4:01 - 5:00 | 8.69 | 8.96 | 9.66 | 7.97
5:01 - 6:00 | 8.69 | 8.96 | 9.66 | 7.97
6:01 - 7:00 | 15.22 | 15.67 | 16.91 | 13.94
7:01 - 8:00 | 23.91 | 24.63 | 26.57 | 21.91
8:01 - 9:00 | 30.43 | 31.35 | 33.82 | 27.88
9:01 - 10:00 | 139.11 | 143.31 | 154.6 | 127.45
10:01 - 11:00 | 184.76 | 190.33 | 205.33 | 169.27
11:01 - 12:00 | 189.11 | 194.81 | 210.16 | 173.26
12:01 - 13:00 | 195.63 | 201.53 | 217.41 | 179.23
13:01 - 14:00 | 210.84 | 217.2 | 234.32 | 193.17
14:01 - 15:00 | 217.37 | 223.92 | 241.57 | 199.14
15:01 - 16:00 | 217.37 | 223.92 | 241.57 | 199.14
16:01 - 17:00 | 204.32 | 210.49 | 227.07 | 187.2
17:01 - 18:00 | 193.46 | 199.29 | 214.99 | 177.24
18:01 - 19:00 | 123.9 | 127.64 | 137.69 | 113.51
19:01 - 20:00 | 58.69 | 60.46 | 65.22 | 53.77
20:01 - 21:00 | 49.99 | 51.5 | 55.56 | 45.8
21:01 - 22:00 | 41.3 | 42.55 | 45.9 | 37.84
22:01 - 23:00 | 36.95 | 38.07 | 41.07 | 33.85
23:01 - 24:00 | 26.08 | 26.87 | 28.99 | 23.9
Cooling Load (tons) vs. Hour/day |  |  |  | 
Hour | J | J | A | S
0:01 - 1:00 | 100 | 100 | 100 | 100
1:01 - 2:00 | 100 | 100 | 100 | 100
2:01 - 3:00 | 100 | 100 | 100 | 100
3:01 - 4:00 | 100 | 100 | 100 | 100
4:01 - 5:00 | 100 | 100 | 100 | 100
5:01 - 6:00 | 100 | 100 | 100 | 100
6:01 - 7:00 | 100 | 100 | 100 | 100
7:01 - 8:00 | 100 | 100 | 100 | 100
8:01 - 9:00 | 100 | 100 | 100 | 100
9:01 - 10:00 | 39.11 | 43.31 | 54.6 | 27.45
10:01 - 11:00 | 84.76 | 90.33 | 105.33 | 69.27
11:01 - 12:00 | 89.11 | 94.81 | 110.16 | 73.26
12:01 - 13:00 | 95.63 | 101.53 | 117.41 | 79.23
13:01 - 14:00 | 110.84 | 117.2 | 134.32 | 93.17
14:01 - 15:00 | 117.37 | 123.92 | 141.57 | 99.14
15:01 - 16:00 | 117.37 | 123.92 | 141.57 | 99.14
16:01 - 17:00 | 104.32 | 110.49 | 127.07 | 87.2
17:01 - 18:00 | 93.46 | 99.29 | 114.99 | 77.24
18:01 - 19:00 | 123.9 | 127.64 | 137.69 | 113.51
19:01 - 20:00 | 58.69 | 60.46 | 65.22 | 53.77
20:01 - 21:00 | 49.99 | 51.5 | 55.56 | 45.8
21:01 - 22:00 | 41.3 | 42.55 | 45.9 | 37.84
22:01 - 23:00 | 100 | 100 | 100 | 100
23:01 - 24:00 | 100 | 100 | 100 | 100
Without Storage
With Storage

## Slide 16
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 2
Regulated Energy Cost
Additional Pumping Cost
Charge/Discharge Tank
Total Annual Operating Cost
Natural Gas Cost Analysis |  |  |  |  |  |  |  |  |  |  |  | 
Month | J | F | M | A | M | J | J | A | S | O | N | D
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Therm/day | 5.1 | 5.08 | 4.19 | 3.19 | 2.92 | 25.24 | 25.55 | 26.37 | 28.03 | 4.29 | 4.87 | 5.41
Therm/month | 158.06 | 142.36 | 129.86 | 95.81 | 90.37 | 757.31 | 792.01 | 817.43 | 841 | 133.08 | 146.06 | 167.57
Cost/Therm | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
Cost/Month | 155.4 | 139.96 | 127.67 | 94.2 | 88.84 | 744.56 | 778.67 | 803.66 | 826.84 | 130.84 | 143.6 | 164.75
Base/Month | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Total/Month | 185.4 | 169.96 | 157.67 | 124.2 | 118.84 | 774.56 | 808.67 | 833.66 | 856.84 | 160.84 | 173.6 | 194.75
Total | 4559 |  |  |  |  |  |  |  |  |  |  | 
Existing Pump Cost | 8265.62 |  |  |  |  |  |  |  |  |  |  | 
Additional Pump Cost | 4820 |  |  |  |  |  |  |  |  |  |  | 
Total System Cost | $17,644.62 |  |  |  |  |  |  |  |  |  |  | 
$12,825
$1,880
$2,940
$17,645

## Slide 17
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Existing Centrifugal Chillers
Chilled Water Storage
2 sizing strategies
    12 hour charge / 12 hour discharge
    12 hour charge / 6 hour discharge
Alternative 3

## Slide 18
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 3
12 hour charge, 12 hour discharge
2,900 ton tank, direct interface
~246,000 gallons
Chiller Output (tons) vs. Hour/day |  |  |  |  |  |  |  |  |  |  |  | 
Hour | J | F | M | A | M | J | J | A | S | O | N | D
0:01 - 1:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
1:01 - 2:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
2:01 - 3:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
3:01 - 4:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
4:01 - 5:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
5:01 - 6:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
6:01 - 7:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0
7:01 - 8:00 | 6.6 | 6 | 6.4 | 5.6 | 6.4 | 270 | 270 | 270 | 270 | 6.7 | 6.2 | 6.3
8:01 - 9:00 | 8.4 | 7.6 | 8.1 | 7.2 | 8.1 | 270 | 270 | 270 | 270 | 8.5 | 7.9 | 8
9:01 - 10:00 | 39 | 35 | 37 | 33 | 37 | 0 | 0 | 0 | 0 | 39 | 36 | 37
10:01 - 11:00 | 51 | 46 | 49 | 43 | 49 | 0 | 0 | 0 | 0 | 52 | 48 | 49
11:01 - 12:00 | 52 | 47 | 50 | 44 | 51 | 0 | 0 | 0 | 0 | 53 | 49 | 50
12:01 - 13:00 | 54 | 49 | 52 | 46 | 52 | 0 | 0 | 0 | 0 | 55 | 51 | 51
13:01 - 14:00 | 58 | 53 | 56 | 50 | 56 | 0 | 0 | 0 | 0 | 59 | 55 | 55
14:01 - 15:00 | 60 | 54 | 58 | 51 | 58 | 0 | 0 | 0 | 0 | 61 | 56 | 57
15:01 - 16:00 | 60 | 54 | 58 | 51 | 58 | 0 | 0 | 0 | 0 | 61 | 56 | 57
16:01 - 17:00 | 57 | 51 | 54 | 48 | 55 | 0 | 0 | 0 | 0 | 57 | 53 | 54
17:01 - 18:00 | 54 | 48 | 52 | 46 | 52 | 0 | 0 | 0 | 0 | 54 | 50 | 51
18:01 - 19:00 | 34 | 31 | 33 | 29 | 33 | 0 | 0 | 0 | 0 | 35 | 32 | 33
19:01 - 20:00 | 16 | 15 | 16 | 14 | 16 | 0 | 0 | 0 | 0 | 16 | 15 | 15
20:01 - 21:00 | 14 | 13 | 13 | 12 | 13 | 0 | 0 | 0 | 0 | 14 | 13 | 13
21:01 - 22:00 | 11 | 10 | 11 | 9.7 | 11 | 270 | 270 | 270 | 270 | 12 | 11 | 11
22:01 - 23:00 | 10 | 9.3 | 9.9 | 8.7 | 9.9 | 270 | 270 | 270 | 270 | 10 | 9.6 | 9.7
23:01 - 24:00 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 270 | 270 | 0 | 0 | 0

## Slide 19
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
Alternative 3
12 hour charge, 6 hour discharge
1,800 ton tank, direct interface
~153,000 gallons
Chiller Output (tons) vs. Hour/day |  |  |  |  |  |  |  |  |  |  |  | 
Hour | J | F | M | A | M | J | J | A | S | O | N | D
0:01 - 1:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
1:01 - 2:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
2:01 - 3:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
3:01 - 4:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
4:01 - 5:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
5:01 - 6:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
6:01 - 7:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0
7:01 - 8:00 | 6.62 | 5.99 | 6.37 | 5.62 | 6.39 | 165 | 165 | 165 | 165 | 6.7 | 6.18 | 6.29
8:01 - 9:00 | 8.43 | 7.62 | 8.11 | 7.16 | 8.13 | 165 | 165 | 165 | 165 | 8.53 | 7.87 | 8.01
9:01 - 10:00 | 38.52 | 34.85 | 37.07 | 32.72 | 37.19 | 139.11 | 143.31 | 154.6 | 127.45 | 38.97 | 35.98 | 36.61
10:01 - 11:00 | 51.16 | 46.28 | 49.23 | 43.46 | 49.39 | 184.76 | 190.33 | 205.33 | 169.27 | 51.76 | 47.79 | 48.62
11:01 - 12:00 | 52.37 | 47.37 | 50.39 | 44.48 | 50.55 | 189.11 | 194.81 | 210.16 | 173.26 | 52.98 | 48.91 | 49.77
12:01 - 13:00 | 54.17 | 49 | 52.13 | 46.02 | 52.3 | 0 | 0 | 0 | 0 | 54.8 | 50.6 | 51.48
13:01 - 14:00 | 58.39 | 52.81 | 56.18 | 49.59 | 56.36 | 0 | 0 | 0 | 0 | 59.07 | 54.53 | 55.49
14:01 - 15:00 | 60.19 | 54.45 | 57.92 | 51.13 | 58.11 | 0 | 0 | 0 | 0 | 60.89 | 56.22 | 57.2
15:01 - 16:00 | 60.19 | 54.45 | 57.92 | 51.13 | 58.11 | 0 | 0 | 0 | 0 | 60.89 | 56.22 | 57.2
16:01 - 17:00 | 56.58 | 51.18 | 54.44 | 48.06 | 54.62 | 0 | 0 | 0 | 0 | 57.24 | 52.85 | 53.77
17:01 - 18:00 | 53.57 | 48.46 | 51.55 | 45.5 | 51.71 | 0 | 0 | 0 | 0 | 54.2 | 50.04 | 50.91
18:01 - 19:00 | 34.31 | 31.03 | 33.01 | 29.14 | 33.12 | 123.9 | 127.64 | 137.69 | 113.51 | 34.71 | 32.05 | 32.61
19:01 - 20:00 | 16.25 | 14.7 | 15.64 | 13.8 | 15.69 | 58.69 | 60.46 | 65.22 | 53.77 | 16.44 | 15.18 | 15.44
20:01 - 21:00 | 13.84 | 12.52 | 13.32 | 11.76 | 13.36 | 49.99 | 51.5 | 55.56 | 45.8 | 14.01 | 12.93 | 13.16
21:01 - 22:00 | 11.44 | 10.34 | 11 | 9.71 | 11.04 | 165 | 165 | 165 | 165 | 11.57 | 10.68 | 10.87
22:01 - 23:00 | 10.23 | 9.26 | 9.85 | 8.69 | 9.88 | 165 | 165 | 165 | 165 | 10.35 | 9.56 | 9.72
23:01 - 24:00 | 0 | 0 | 0 | 0 | 0 | 165 | 165 | 165 | 165 | 0 | 0 | 0

## Slide 20
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
designing the system
12-hour discharge
  Regulated Energy Cost
6-hour discharge
  Regulated Energy Cost
246,000 gal Cost Analysis |  |  |  |  |  |  |  |  |  |  |  | 
Month | J | F | M | A | M | J | J | A | S | O | N | D
Max Demand | 50.38 | 45.57 | 48.48 | 42.79 | 48.64 | 225.99 | 225.99 | 225.99 | 225.99 | 50.97 | 47.06 | 47.88
Demand Charge | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 9.17 | 9.17 | 9.17 | 9.17 | 0.5 | 0.5 | 0.5
$/month | 25.19 | 22.79 | 24.24 | 21.4 | 24.32 | 2072.33 | 2072.33 | 2072.33 | 2072.33 | 25.48 | 23.53 | 23.94
$/day | 31.44 | 28.43 | 30.25 | 26.7 | 30.35 | 174.43 | 174.43 | 174.43 | 174.43 | 31.8 | 29.36 | 29.87
days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Consumption Cost | 974.49 | 796.2 | 937.7 | 801.1 | 940.7 | 5232.78 | 5407.2 | 5407.2 | 5232.78 | 985.8 | 880.8 | 926.1
Total Cost | 37003.2 |  |  |  |  |  |  |  |  |  |  | 
153,000 gal Cost Analysis |  |  |  |  |  |  |  |  |  |  |  | 
Month | J | F | M | A | M | J | J | A | S | O | N | D
Max Demand | 50.38 | 45.57 | 48.48 | 42.79 | 48.64 | 158.28 | 163.06 | 175.91 | 145.01 | 50.97 | 47.06 | 47.88
Demand Charge | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 9.17 | 9.17 | 9.17 | 9.17 | 0.5 | 0.5 | 0.5
$/month | 25.19 | 22.79 | 24.24 | 21.4 | 24.32 | 1451.46 | 1495.24 | 1613.06 | 1329.78 | 25.48 | 23.53 | 23.94
$/day | 31.44 | 28.43 | 30.25 | 26.7 | 30.35 | 159.17 | 160.75 | 165.02 | 154.76 | 31.8 | 29.36 | 29.87
days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Consumption Cost | 974.49 | 796.2 | 937.7 | 801.1 | 940.7 | 4775.04 | 4983.37 | 5115.68 | 4642.82 | 985.8 | 880.8 | 926.1
Total Cost | 32,840.19 |  |  |  |  |  |  |  |  |  |  | 
Alternative 3
$37,000
$33,000

## Slide 21
Chart: CO2 Emssions (pounds)
| J | F | M | A | M | J | J | A | S | O | N | D
Existing System | 56456.8408 | 46124.5658 | 54324.0652 | 46408.2963 | 54499.8556 | 207425.3752 | 220804.5938 | 238204.2011 | 190037.057 | 57114.2487 | 51030.8225 | 53652.4399
Alternative 1 | 23016.4353 | 20728.2549 | 18909.117 | 13953.0273 | 13158.9689 | 56466.649 | 60108.8259 | 64845.457 | 70052.1383 | 19377.6176 | 21268.0157 | 24401.0989
Alternative 2 | 23016.4353 | 20728.2549 | 18909.117 | 13953.0273 | 13158.9689 | 110279.3655 | 115348.837 | 119056.2591 | 122451.1378 | 19377.6176 | 21268.0157 | 24401.0989
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
payback analysis
designing the system
Simple Payback
Payback Period
Component |  |  | First Cost | Additional First Cost | Annual Maintanence
Control | Chiller | Carrier 19XR | 63,000 | - | 4,000
 | Chiller | Carrier 19XR | 63,000 |  | 4,000
Alternative 1 | Absorption Chiller | Carrier 16LJ | 103,000 | 346,625 | 6,000
 | Absorption Chiller | Carrier 16LJ | 103,000 |  | 6,000
 | Boiler | RBI Futera XLF | 52,000 |  | 500
 | Boiler | RBI Futera XLF | 52,000 |  | 500
 | Solar Absorbers (425) |  | 225,625 |  | 1,000
 | Additional Pumps | B&G | 4,000 |  | --
Alternative 2 | Absorption Chiller | Carrier 16LJ | 103,000 | 430,050 | 6,000
 | Absorption Chiller | Carrier 16LJ | 103,000 |  | 6,000
 | Boiler | RBI Futera XLF | 52,000 |  | 500
 | Boiler | RBI Futera XLF | 52,000 |  | 500
 | Solar Absorbers (290) |  | 187,050 |  | 1,000
 | 900 ton Storage Tank |  | 82,000 |  | --
 | Additional Pumps | B&G | 7,000 |  | --
Alternative 3a | Chiller | Carrier 19XR | 63,000 | 301,000 | 4,000
 | Chiller | Carrier 19XR | 63,000 |  | 4,000
 | 2,900 ton Storage Tank |  | 295,000 |  | --
 | Additional Pumps | B&G | 6,000 |  | --
Alternative 3b | Chiller | Carrier 19XR | 63,000 | 246,000 | 4,000
 | Chiller | Carrier 19XR | 63,000 |  | 4,000
 | 1,650 ton Storage Tank |  | 240,000 |  | --
 | Additional Pumps | B&G | 6,000 |  | --
Simple Payback Calculation |  | 
 | Alternative 1 | Alternative 2
Additional First Cost | 346,625 | 430,050
Additional Maintenance Cost | 6,000 | 6,000
Annual Savings | 19,700 | 17,185
Payback Period | 17.60 | 25.02
What if?
Hoover dam dries up
Coal must be used to generate electricity
CO2 credits could reduce payback periods
CO2 Emissions
Alternative 1: 870,000 pounds less
Alternative 2: 655,000 pounds less

## Slide 22
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
depth summary
payback analysis
The existing system achieved its design objectives and achieved LEED Gold
Alternative 1 - 17,000 ft2 of absorbers
Alternative 2 – 11,600 ft2 of absorbers
        chilled water storage
Alternative 3 – chilled water storage
Innovative and Energy Efficiency
Chart: Cost ($)
| J | F | M | A | M | J | J | A | S | O | N | D
Control | 999.68 | 818.94 | 961.92 | 822.45 | 965.03 | 6693.33 | 7067.77 | 7624.72 | 6132.23 | 1011.32 | 904.37 | 950.03
Alternative 1 | 903.7223 | 828.4162 | 770.121 | 604.3987 | 580.0278 | 2003.289 | 2125.144 | 2280.338 | 2451.665 | 783.9636 | 848.1079 | 950.4657
Alternative 2 | 717.5264 | 657.7712 | 610.2071 | 480.673 | 459.929 | 2997.666 | 3129.677 | 3226.392 | 3316.102 | 622.4754 | 671.8586 | 753.7123
The existing system achieved its design objectives and achieved LEED Gold
Alternative 1 - $15,130, 17.6 year payback
Alternative 2 – $17,645, 25 year payback
Alternative 3 – No annual savings

## Slide 23
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
structural breadth
depth summary
Existing Roof Structure
Non-composite (2C 22)
5” depth
7 ft. spans
98 psf (Vulcraft)
7’1” max clearspan
Roof System
Roof Loads | 
Description | Weight (psf)
Mech./Elec./Plumbing | 10
Roof Mat | 20
Slab/Deck (2C22) | 50
Miscellaneous | 5
Beams/Joists | 10
Total | 95
Solar absorbers: 12.5 psf
Reduce Joist Spacing
  6’6”: 113 psf
  Use 2C 22 at 6’ spacing
Increase Deck Strength
2C 20
127 psf
8’6” max clearspan

## Slide 24
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
construction breadth
structural breadth
Thermal Storage Tanks
Calculation shows an extra 20-30 ft. needed
Mechanical Yard
Cooling Tower
Cooling Tower
Other Equipment
Cooling Tower
Cooling Tower
Other Equipment
Thermal Storage Tank
Cost Analysis |  |  |  |  |  | 
 | Component |  | Material | Labor | Equipment | Total
20 ft. Extension | Strip Footer | 12" x 12" | 259.26 | 26.31 | 0.86 | 286.43
 | Slab | 6" | 1111.11 | 159.44 | 5.00 | 1275.56
 | Wire Fabric | 6x6 | 195.00 | 147.00 | 0.00 | 342.00
 | CMU Wall | 12" x 10ft. | 2169.60 | 3360.00 | 0.00 | 5529.60
 | Formwork |  | 22.40 | 135.10 | 0.00 | 157.50
 | Total Cost |  |  |  |  | 7591.09
30 ft. Extension | Strip Footer | 12" x 12" | 333.33 | 33.83 | 1.10 | 368.27
 | Slab | 6" | 1666.67 | 239.17 | 7.50 | 1913.33
 | Wire Fabric | 6x6 | 292.50 | 220.50 | 0.00 | 513.00
 | CMU Wall | 12" x 10ft. | 3254.40 | 5040.00 | 0.00 | 8294.40
 | Formwork |  | 28.80 | 173.70 | 0.00 | 202.50
 | Total Cost |  |  |  |  | 11291.50
 | Days of Work | 
 | 20 ft. Extension | 30 ft. Extension
Strip Footer | 0.05 | 0.06
Formwork | 0.13 | 0.15
Wire Fabric | 0.21 | 0.31
Slab | 0.19 | 0.28
Subtotal | 1 | 1
CMU Wall | 2.4 | 3.6
Total | 3.5 | 5

## Slide 25
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
conclusions
construction breadth
Control
Alternative 1
Alternative 2
Do, or not to do?
lowest initial cost
most energy savings
heaviest roof load
$19,700 cost savings
longer payback
larger mechanical yard
Innovation and Energy Efficiency
“Alternative 1 would not only achieve these goals, but exceed them.”

## Slide 26
Introduction
Project History
Existing Systems
Improving the System
Designing the System
Payback Analysis
Depth Summary
Structural Breadth
Construction Breadth
Conclusions
Q & A
questions? and maybe some answers
conclusions
Acknowledgements
Advisors: Dr. James Freihaut
Dr. William Bahnfleth
Sponsors: Vanderweil Engineers
State of Nevada Public Works
PSU Students: Thomas Chirdon
Scott Earley
Dominic Manno
Special Thanks to: Bruce Nipp
Fred Livingston, Steve Germano,
and the rest of the
Vanderweil Las Vegas office