## Slide 1: SENIOR THESIS PRESENTATION
Grey-water Reheat with Combined Heat and Power Analysis for a Hotel
Hotel Felix
Chicago, Illinois
The Pennsylvania State University
Department of Architectural Engineering
Presented by
Geoffrey Kim | Mechanical
AE 482 Senior Thesis | Faculty Advisor: Dr. Jelena Srebric

## Slide 2: BUILDING OVERVIEW
BUILDING NAME: HOTEL FELIX
LOCATION : CHICAGO, ILLINOIS
SIZE: 85,700 SF
HEIGHT: 12 STORIES
RENOVATION: SEP.2007 – MARCH 2009
LEED SILVER CERTIFIED
HOTEL FELIX
INTRODUCTION
HOTEL FELIX

## Slide 3: SITE MAP
HOTEL FELIX
INTRODUCTION
HOTEL FELIX

## Slide 4: SITE MAP
HOTEL FELIX
INTRODUCTION
HOTEL FELIX
W Chicago Ave.
N Lasalle Dr.
N Michigan Ave
HOTEL FELIX

## Slide 5: EXISTING MECHANICAL SYSTEM
(1) Roof Top Air Handling Unit
(1) Self Contained Unit
(225) Water Source Heat Pumps
(1) Split System Air Conditioning Unit
(1) Gas Fired Unit Heater
HOTEL FELIX
INTRODUCTION
HOTEL FELIX

## Slide 6: EXISTING MECHANICAL SYSTEM
HOTEL FELIX
INTRODUCTION
HOTEL FELIX
Zone 1 (Guest Rooms) Water Source Heat Pumps
Zone 3 (Corridor) Constant Volume RTU
Zone 2 (Basement, Ground, Mezzanine Floor) VAV Terminal Boxes w/ Electric Reheat

## Slide 7: DESIGN OBJECTIVES
Lower Annual Energy Utilization
Lower Impact on the Environment
Investigate Greywater Heat Recovery System and Combined Heating and Power.
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX

## Slide 8: GREYWATER HEAT RECOVERY SYSTEM
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
BOILER
GREYWATER
HEAT EXCHANGER
HOT WATER FROM BOILER (140F)
COLD WATER FOR BOILER (54F)
PREHEATED
COLD WATER
SHOWER
DRAIN WATER (110F)

## Slide 9: GREYWATER HEAT RECOVERY SYSTEM
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
 | Hotel Room Showers
Cold Water Supply (0F) | 54
Hot Water Leaving Boiler (0F) | 140
Temperature of Shower (0F) | 110
Efficiency of Boiler + Hot Water Pipes | 80 %
Thermal Capacity of Water (btu/ft3 0F) | 62.4
Energy to heat one gallon of shower water (Btu/gallon) | 585
 | Hotel Room Showers
Typical Shower Flow Rate (GPM) | 2.5
Average Length of Shower (Min) | 5
Number of Showers (225) | 225
Number of Showers per Day per Room | 2
Daily Shower Water Usage (gallons/day) | 6875
Estimated Hotel Occupancy | 70%
Estimated Daily Shower Water Usage (gallons) | 4812
 | Hotel Room Showers
Energy required to heat water per day (btu/day) | 4,024,020
Natural Gas Price ($/therm) | 0.836
Annual cost (per year) | 12,279

## Slide 10: GREYWATER HEAT RECOVERY SYSTEM
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Energy Reduction Annual Energy Consumption 14,673 therms Annual Energy Savings 4,324 therms Percentage Reduction 29.5% Savings
Savings Annual Energy Savings 4,324 therm/year Annual Cost Savings $5,188 / year

## Slide 11: GREYWATER HEAT RECOVERY SYSTEM
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Initial Equipment Cost Heat Exchanger $27,540 Piping + Labor $6,400 Total =$33,940
Payback Period $33,940 / $5,188 = 6.54 Years

## Slide 12: COMBINED HEAT AND POWER
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
PRIME MOVER
GENERATOR
EXHAUST HEAT
ELECTRICITY
THERMAL OUTPUT
WASTE ENERGY
FUEL

## Slide 13: COMBINED HEAT AND POWER
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Prime Mover Selection
Internal Combustion Engine Heat: Power Ratio - 1:1 Capacity – up to 4MW
Micro Turbine Heat : Power Ratio – 2:1 Capacity – Up to 1MW

## Slide 14: COMBINED HEAT AND POWER
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Chart: 
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
 | 8911 | 6210 | 5000 | 3100 | 3300 | 4500 | 4850 | 4750 | 4250 | 3894 | 4450 | 6600
Monthly Utility Cost
DOLLARS ($)

## Slide 15: COMBINED HEAT AND POWER
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Initial Equipment Cost Microturbine ($1500/kW) $45,000 Labor ($400/kW) $12,000 Ductwork and Piping ($100/kW) $3,000 Total =$60,000

## Slide 16: COMBINED HEAT AND POWER
HOTEL FELIX
MECHANICAL REDESIGN
HOTEL FELIX
Energy Savings Annual Cost Saving $6,355 Initial Cost $60,000
Simple Payback Period 9.5 Years

## Slide 17: ACOUSTIC ANALYSIS
HOTEL FELIX
Acoustic Analysis
HOTEL FELIX
Design Criteria
CHP system noise to not exceed 40 NC to Hotel Room Below
CHP System to Meet Chicago Noise Ordinance Code

## Slide 18: ACOUSTIC ANALYSIS
HOTEL FELIX
Acoustic Analysis
HOTEL FELIX
Existing Roof – Concrete slab roof w/ steel joists
Chart: Noise Criteria
Hotel Room | 52 | 36 | 31 | 22 | 12 | 0 | 0 | 0
NC-65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
NC-60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC-55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC-50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC-45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC-40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
Nc-35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC-30 | 57 | 48 | 41 | 36 | 31 | 29 | 28 | 27
NC-25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC-20 | 51 | 40 | 33 | 26 | 22 | 19 | 17 | 16
NC-15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11

## Slide 19: CONCLUSION
HOTEL FELIX
Conclusion
HOTEL FELIX
Greywater Reheat Annual Saving $5,188
Payback Period 6.5 Years
CHP System Annual Saving $6,355
Payback Period 9.5 Years

## Slide 20: ACKNOWLEDGEMENTS
HOTEL FELIX
Acknowledgements
HOTEL FELIX
Professor Holland
Professor Srebric
Professor Freihaut
Professor Ling
Leland Curtis
Trien Devon Lam
Shiyun Chen
AE Faculty, and Friends, and Dewberry