## Slide 1
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York

## Slide 2
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Presentation Outline
  Introduction
Location, Statistics, General Information
John M. Scavelli
The Pennsylvania State University
Architectural Engineering
Mechanical Option
Master of Architectural Engineering
Bachelor of Architectural Engineering
Thesis Advisor: Dr. William Bahnfleth
Introduction
Presentation Plan

## Slide 3
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
John M. Scavelli
The Pennsylvania State University
Architectural Engineering
Mechanical Option
Master of Architectural Engineering
Bachelor of Architectural Engineering
Thesis Advisor: Dr. William Bahnfleth
Introduction
Presentation Plan

## Slide 4
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
John M. Scavelli
The Pennsylvania State University
Architectural Engineering
Mechanical Option
Master of Architectural Engineering
Bachelor of Architectural Engineering
Thesis Advisor: Dr. William Bahnfleth
Introduction
Presentation Plan

## Slide 5
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation
John M. Scavelli
The Pennsylvania State University
Architectural Engineering
Mechanical Option
Master of Architectural Engineering
Bachelor of Architectural Engineering
Thesis Advisor: Dr. William Bahnfleth
Introduction
Presentation Plan

## Slide 6
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Building Location
Location
College Point, New York
North Eastern Part of the United States of America
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 7
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Building Location
Location
College Point, New York
Close Proximity to Manhattan, NY
NYPA
Manhattan
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 8
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Building Location
Location
College Point, New York
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 9
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Building Statistics
Occupant: New York Police Department
Architect: Perkins + Will
Site Size: 2,400,000 SF
Building Size: 840,400 SF
Overall Cost: $656,000,000
East Campus: Academic/Office Space
  375,405 SF
West Campus: Physical Fitness/ Central Plant
  465,000 SF
Architecture: Modern w/ Strong Geometric Forms
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 10
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
General Information
General Construction Information
General Structural Information
Turner Construction Company and STV Inc. will lead as joint General Contractors.
New York Department of Design and Construction will be responsible for overseeing the progression of the project.
Structural Engineers : Robert Silman Associates
Steel Super Structure
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation
General Electrical Information
Electrical Engineers: WSP Flack + Kurtz
460/265V 3-Phase High Voltage system stepped down to 120/208 V 3-Phase Low Voltage System
General Mechanical Information
Mechanical Engineers: WSP Flack + Kurtz
Centralized Heating and Cooling Plant System

## Slide 11
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Mechanical Systems Overview
Ventilation Needs
  63 Air Handling Units-3,000-30,000 CFM
    18-Central Plant
    26-West Campus
    19-East Campus
Central Plant-Heating and Cooling
  6- 1350 Ton Electric Centrifugal Chillers
    2 Installed for future expansion
  6- Induced Draft Cooling Towers
    3 Installed for future expansion
  5-25110 MBH Natural Gas Water Tube Boilers
    2 Installed for Future expansion
Central Plant
West Campus
East Campus
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 12
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Mechanical Systems Overview
Ventilation Needs
  63 Air Handling Units-3,000-30,000 CFM
    18-Central Plant
    26-West Campus
    19-East Campus
Central Plant-Heating and Cooling
  6- 1350 Ton Electric Centrifugal Chillers
    2 Installed for future expansion
  6- Induced Draft Cooling Towers
    3 Installed for future expansion
  5-25110 MBH Natural Gas Water Tube Boilers
    2 Installed for Future expansion
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 13
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Mechanical Systems Overview
Ventilation Needs
  63 Air Handling Units-3,000-30,000 CFM
    18-Central Plant
    26-West Campus
    19-East Campus
Central Plant-Heating and Cooling
  6- 1350 Ton Electric Centrifugal Chillers
    2 Installed for future expansion
  6- Induced Draft Cooling Towers
    3 Installed for future expansion
  5-25110 MBH Natural Gas Water Tube Boilers
    2 Installed for Future expansion
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 14
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
East Campus Building Loads
The East Campus was chosen as the specific building of study.
  East and West Campus essentially two separate buildings
  375,405 SF
TRANE Trace 700 Used
  Location: LaGuardia Airport (1.6 miles from NYPA)
  Block Load Analysis
  52 Zones
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 15
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
East Campus Energy Consumption
The East Campus was chosen as the specific building of study.
  East and West Campus essentially two separate buildings
  375,405 SF
TRANE Trace 700 Used
  Location: LaGuardia Airport (1.6 miles from NYPA)
  Block Load Analysis
  52 Zones
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 16
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
East Campus Energy Utility Costs
The East Campus was chosen as the specific building of study.
  East and West Campus essentially two separate buildings
  375,405 SF
TRANE Trace 700 Used
  Location: LaGuardia Airport (1.6 miles from NYPA)
  Block Load Analysis
  52 Zones
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 17
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Alternative Design Proposal
Mechanical Depth:
East Campus
Ground Source Heat Pump System
Electrical Breadth:
Photovoltaic System
Construction Management Breadth:
GSHP Cost, Labor, Schedule Impact

## Slide 18
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Mechanical Depth Proposal
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 19
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
GSHP System Justification
  Reduce Size of Central Plant yet keep ability for future expansion for West Campus.
    East Campus will not be expanded upon.
  High Electricity Costs in New York
    Reduce Energy Consumption
      Therefore, reduce utility costs and emissions
  New Construction Project
  Large enough site for well field
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 20
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
GSHP System Schematics
Original Central Plant Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 21
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
GSHP System Schematics
Original Central Plant Design
GSHP Major Discussion Topics
GSHP Design
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 22
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
GSHP Loop Sizing
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
  Calculated using ASHRAE’s Handbook: HVAC Applications (Chapter 32)
  Largest length required would be for cooling: 299,183 ft.
  Cost Optimization of Loop Size( will be discussed under CM Breadth)
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 23
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Energy Modeling
GSHP Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 24
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Utility Cost Comparison
GSHP Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
  17% Annual Utility Savings
    Electricity + Natural Gas
  Annual Savings: $171,147
    Life Cycle Analysis
  will be evaluated after
  construction (first) costs are
  established
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 25
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Utility Cost Comparison
GSHP Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Energy Modeling
  Utility Cost Comparison
  17% Annual Utility Savings
    Electricity + Natural Gas
  Annual Savings: $171,147
    Life Cycle Analysis
  will be evaluated after
  construction (first) costs are
  established
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation
$
$
$

## Slide 26
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Alternative Design Proposal
Mechanical Depth:
East Campus
Ground Source Heat Pump System
Electrical Breadth:
Photovoltaic System
Construction Management Breadth:
GSHP Cost, Labor, Schedule Impact
Photovoltaic System Discussion Topics

## Slide 27
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Electrical Breadth Proposal
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Photovoltaic Array on West Campus Roof
Prior to PV Array
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 28
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Electrical Breadth Proposal
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Photovoltaic Array on West Campus Roof
Prior to PV Array
W/ PV Array
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 29
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Array Size
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 30
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Electrical Characteristics
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 31
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Economic Analysis
Photovoltaic System Discussion Topics
  5% of Electricity
  0.2% Increase in Cost
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis

## Slide 32
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Economic Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 33
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Economic Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 34
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Alternative Design Proposal
Mechanical Depth:
East Campus
Ground Source Heat Pump System
Electrical Breadth:
Photovoltaic System
Construction Management Breadth:
GSHP Cost, Labor, Schedule Impact
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics

## Slide 35
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Length Optimization
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 36
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Length Optimization
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Provides over 100% of Heating Load
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 37
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Length Optimization
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Unused Capacity
Under Capacity
Provides over 100% of Heating Load
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 38
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Length Optimization
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Supplement with/ Cooling Tower
Optimum Cost
Unused Capacity
Under Capacity
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 39
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Construction Cost
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 40
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
GSHP Life Cycle Cost Analysis
  Length Optimization
  Construction Cost
  Life Cycle Cost Analysis
Construction Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 41
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
The Final Analysis
Mechanical Depth:
East Campus
Ground Source Heat Pump System
Electrical Breadth:
Photovoltaic System
Construction Management Breadth:
GSHP Cost, Labor, Schedule Impact
Final Analysis
  Yearly Cost Analysis: GSHP + PV System
  Life Cycle Cost Analysis: GSHP + PV System
  Pros vs. Cons
  Final Recommendations

## Slide 42
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Yearly Cost Analysis: GSHP + PV System
Final Analysis
  Yearly Cost Analysis: GSHP + PV System
  Life Cycle Cost Analysis: GSHP + PV System
  Pros vs. Cons
  Final Recommendations
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 43
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Life Cycle Cost Analysis
Final Analysis
  Yearly Cost Analysis: GSHP + PV System
  Life Cycle Cost Analysis: GSHP + PV System
  Pros vs. Cons
  Final Recommendations
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 44
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Pros vs. Cons
Pros
Reduced Emissions
Reduced Utility Costs
Sustainable Landmark Building
Eliminate Natural Gas Consumption
Decrease Electricity Demand
Cons
Increase in First Costs
Ground Temp Increase
Construction Difficulty
  Final Recommendations
    GSHP Implementation: Affirmative
    Photovoltaic Implementation: Affirmative
Final Analysis
  Yearly Cost Analysis: GSHP + PV System
  Life Cycle Cost Analysis: GSHP + PV System
  Pros vs. Cons
  Final Recommendations
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 45
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Thank You for Listening
Special Thanks to:
Turner Construction Company
Penn State Architectural Engineering Faculty, Staff, and Students

## Slide 46
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Questions?

## Slide 47
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
New York Police Academy
College Point, New York
Appendix

## Slide 48
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Well Field Layout
GSHP Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Well Field Layout
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 49
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Well Field Layout
GSHP Design
GSHP Major Discussion Topics
  Justification
  System Schematics
  Ground Source Heat Pump Loop Sizing
  Well Field Layout
  Energy Modeling
  Utility Cost Comparison
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 50
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Well Field Layout
GSHP Design
  214 Wells
  Depth 350’
  Two Loops per well
Well Field Layout |  | 
Row | # of Wells | Capacity
1 | 20 | 9.3%
2 | 20 | 9.3%
3 | 20 | 9.3%
Manifold 1 Total: | 60 | 28%
4 | 22 | 10.3%
5 | 22 | 10.3%
6 | 22 | 10.3%
Manifold 2 Total: | 66 | 31%
7 | 22 | 10.3%
8 | 22 | 10.3%
9 | 22 | 10.3%
10 | 22 | 10.3%
Manifold 3 Total: | 88 | 41%
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 51
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Array Placement
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 52
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Electrical Schematic
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 53
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Panel and Mounting System
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
  Sharp NU Series 185 W Panels
  Solion SunMount System
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 54
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Economic Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 55
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
Economic Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation

## Slide 56
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
CFD Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation
0 meters
5 meters
10 meters
20 meters
30 meters
0 meters

## Slide 57
The Pennsylvania State University: Department of Architectural Engineering
John M. Scavelli Mechanical Option Senior Thesis 2010-2011
Master/Bachelor of Architectural Engineering Student
CFD Analysis
  Array Placement
  Array Size
  Panel Chosen, Mounting System Chosen
  Electrical Characteristics
    Strings, Inverter, Switchgear
  Economic Analysis
Photovoltaic System Discussion Topics
Presentation Outline
  Introduction
Location, Statistics, General Information
  Actual Mechanical Design
System, Loads, Utility Costs
  Alternative Design
Mechanical Depth: GSHP
Electrical Breadth: PV Array
Construction Breadth: Cost Analysis
  The Final Analysis
Integration of Depths & Breadths
Final Recommendation