## Slide 1
New Braunfels Regional Rehabilitation Hospital
Adam Bernardo
Mechanical Option
New Braunfels, TX
Images courtesy of Dekker/Perich/Sabatini Architects

## Slide 2
Images courtesy of Dekker/Perich/Sabatini Architects
PROJECT INTRODUCTION
DEPTH STUDIES
BREADTH STUDY
OVERALL EVALUATION
CONCLUSION / QUESTIONS

## Slide 3
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
PROJECT INTRODUCTION

## Slide 4
AGENDA
PROJECT INTRODUCTION
FACILITY DESCRIPTION
MECHANICAL SYSTEM OVERVIEW
THESIS GOALS
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
FACILITY DESCRIPTION
Function: acute-care rehabilitation hospital
Location: New Braunfels, TX
~30 miles NE of San Antonio
Image courtesy of Bing maps

## Slide 5
AGENDA
PROJECT INTRODUCTION
FACILITY DESCRIPTION
MECHANICAL SYSTEM OVERVIEW
THESIS GOALS
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
FACILITY DESCRIPTION
Spaces:
Function: acute-care rehabilitation hospital
Location: New Braunfels, TX
~30 miles NE of San Antonio
40 Patient Rooms
Exam and Light Procedure Rooms
Kitchen and Dining
Office and Administration
Physical Therapy Gym
Therapy Pool
Service Rooms

## Slide 6
AGENDA
PROJECT INTRODUCTION
FACILITY DESCRIPTION
MECHANICAL SYSTEM OVERVIEW
THESIS GOALS
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
MECHANICAL SYSTEM OVERVIEW
Three rooftop air-handling units
  Air-cooled, DX cooling
  Gas-fired pre-heat
  55,500 CFM Total
VAV terminal units with reheat
  Zone-level reheat coils
    Heating hot water supplied by gas-fired boilers
  Fully ducted return system
MAU and PAC Unit
  100% OA makeup air unit serves kitchen and dining
  PAC Unit controls therapy pool temperature/humidity
Monthly Electrical Energy Consumption

## Slide 7
AGENDA
PROJECT INTRODUCTION
FACILITY DESCRIPTION
MECHANICAL SYSTEM OVERVIEW
THESIS GOALS
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
THESIS GOALS
Investigate systems that could:
Reduce energy use and operating costs
Improve occupant temperature control
Pay back in ~5 years
Have academic benefit

## Slide 8
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
MECHANICAL DEPTH STUDIES
Depth Study 1: Central Plant Investigation
High Efficiency Condensing Boilers
Chilled Water Plant: Air-Cooled vs. Water-Cooled
Hypothesis: Will not be cost-effective
Depth Study 2: Variable Refrigerant Flow System
Heat recovery operation: Reduce annual energy use
Improve zone-level temperature control
Academic benefit: Learn the principles of system operation
Depth Study 3: Solar Thermal System
Reduce domestic hot water and space heating load
Utilize the hot Texas climate
Take advantage of fairly constant domestic hot water demand
Academic benefit: Learn the principles of system operation

## Slide 9
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 1: CENTRAL PLANT INVESTIGATION
Condensing Boilers:
Condense the water vapor produced by combustion to recover latent heat
Increase overall boiler efficiency
Ideal with low return water temperatures
  Varies with load – average range used for model

## Slide 10
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 1: CENTRAL PLANT INVESTIGATION
Decrease in natural gas consumption not significant
97-year simple payback
Monthly Natural Gas Consumption
Condensing Boilers:
Condense the water vapor produced by combustion to recover latent heat
Increase overall boiler efficiency
Ideal with low return water temperatures
  Varies with load – average range used for model

## Slide 11
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 1: CENTRAL PLANT INVESTIGATION
Chilled Water System Design:
Two 90-ton chillers arranged in parallel
Primary-secondary chilled water pumping configuration
Air-Cooled:
Chillers placed outside – no mechanical room space requirement
Less significant first cost increase and energy savings
Water-Cooled:
200-ton cooling tower with associated condenser water loop
Increased equipment cost, increased energy savings
Equipment Energy Use

## Slide 12
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
System Operation:
Several indoor evaporating units connected to one outdoor condensing unit
Refrigerant flow modulated by inverter-driven scroll compressor
  Flow rate controlled by low pressure sensor at suction side of compressor
  Goal: control evaporation temperature to match load on each evaporator
P

## Slide 13
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
Heat recovery operation:
  3-pipe system for simultaneous heating and cooling
COLD REFRIGERANT
SUCTION LINE
HOT REFRIGERANT
System Operation:
Several indoor evaporating units connected to one outdoor condensing unit
Refrigerant flow modulated by inverter-driven scroll compressor
  Flow rate controlled by low pressure sensor at suction side of compressor
  Goal: control evaporation temperature to match load on each evaporator

## Slide 14
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
COLD REFRIGERANT
SUCTION LINE
HOT REFRIGERANT
Heat recovery operation:
  3-pipe system for simultaneous heating and cooling
System Operation:
Several indoor evaporating units connected to one outdoor condensing unit
Refrigerant flow modulated by inverter-driven scroll compressor
  Flow rate controlled by low pressure sensor at suction side of compressor
  Goal: control evaporation temperature to match load on each evaporator

## Slide 15
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
COLD REFRIGERANT
SUCTION LINE
HOT REFRIGERANT
Heat recovery operation:
  3-pipe system for simultaneous heating and cooling
System Operation:
Several indoor evaporating units connected to one outdoor condensing unit
Refrigerant flow modulated by inverter-driven scroll compressor
  Flow rate controlled by low pressure sensor at suction side of compressor
  Goal: control evaporation temperature to match load on each evaporator

## Slide 16
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
COLD REFRIGERANT
SUCTION LINE
HOT REFRIGERANT
Heat recovery operation:
  3-pipe system for simultaneous heating and cooling
System Operation:
Several indoor evaporating units connected to one outdoor condensing unit
Refrigerant flow modulated by inverter-driven scroll compressor
  Flow rate controlled by low pressure sensor at suction side of compressor
  Goal: control evaporation temperature to match load on each evaporator

## Slide 17
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
System Zoning:
System Designed: six condensing units:
All indoor units ducted – connected to a 100% outside air unit for ventilation
RTU-1 can be removed, remaining zones served by existing RTUs 2 & 3

## Slide 18
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
Significant energy savings from cooling and fan energy reduction
System most efficient in summer months – not attributed to heat recovery
System Designed: six condensing units:
All indoor units ducted – connected to a 100% outside air unit for ventilation
RTU-1 can be removed, remaining zones served by existing RTUs 2 & 3

## Slide 19
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 2: VRF SYSTEM
Significant energy savings from cooling and fan energy reduction
System most efficient in summer months – not attributed to heat recovery
System Designed: six condensing units:
All indoor units ducted – connected to a 100% outside air unit for ventilation
RTU-1 can be removed, remaining zones served by existing RTUs 2 & 3
System Added First Cost: $57,442
  + Indoor & Outdoor Units ($53,680)
  + VRF Piping & Distribution ($76,580)
  + Outdoor Air Unit ($23,725)
  + Refrigerant & Controls ($6,600)
  - RTU-1 Eliminated (-$86,502)
    - Roof Framing Cost (-$2,900)
Simple Payback Period: 5.8 years
20-year life-cycle cost: $1,104,911
  (existing system: $1,171,718)*
  *Does Not Include Domestic Hot Water Energy Use
Yearly Savings: $9,906

## Slide 20
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
System Operation:
Primary Functions: Heat domestic hot water &
          Therapy pool heating
  Loads calculated through methods in ASHRAE Handbooks
Thermal storage in hot water storage tank
  Has indirect heater: replaces existing hot water heaters
Secondary Function: Space heating
  Loads from Trace Energy Model
Flat-plate, forced circulation solar collection system
  Glycol-water mixture used in collection loop for freeze protection

## Slide 21
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
Solar Gain Calculation
Based on:
Latitude (Ф = 29.69°N)
Zenith Angle (θz)
Hour Angle (ω)
Hourly dependent
Solar Declination(δ) – Date dependent
Collector Tilt (β)
Surface Azimuth (ϒ)
Collector Characteristics
- optimized at β = 37.2°  40° was used
- optimized at β = 37.5°W  33°W was used
System Operation Characteristics

## Slide 22
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
Solar Gain Calculation
Based on:
Latitude (Ф = 29.69°N)
Zenith Angle (θz)
Hour Angle (ω)
Hourly dependent
Solar Declination(δ) – Date dependent
Collector Tilt (β)
Surface Azimuth (ϒ)
Collector Characteristics
- optimized at β = 37.2°  40° was used
Image courtesy of Bing maps
- optimized at ϒ = 37.5°W  33°W was used
System Operation Characteristics

## Slide 23
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
Collector Arrangement
Area: (3) 130 ft2 collectors  390 ft2 total
Peak Load
Useful Gain
  Goal: maximize total solar fraction:
      without overheating or throwing away energy
Thermal Storage

## Slide 24
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
Load Met Directly:
38% of annual domestic hot water heating load met directly
8% of space heating load met directly
Thermal storage in a 400 gallon stratified hot water tank:
38% of DHW load through storage
76% total

## Slide 25
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
Load Met Directly:
38% of annual domestic hot water heating load met directly
8% of space heating load met directly
Thermal storage in a 400 gallon stratified hot water tank:
38% of DHW load through storage
14% of space heating through storage
76% total
22% total

## Slide 26
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
CENTRAL PLANT INVESTIGATION
VRF SYSTEM
SOLAR THERMAL SYSTEM
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
DEPTH STUDY 3: SOLAR THERMAL SYSTEM
System Added First Cost: $61,906
  + Collectors ($26,758)
  + Storage Tank ($4,670)
  + Heat Exchangers ($8,403)
  + Piping & Distribution Equipment ($1,555)
Simple Payback Period: 2.06 years
20-year life-cycle cost: $1,742,889
  (existing system: $2,070,197)*
  *Includes Domestic Hot Water Energy Use
  + Controls ($10,520)
Yearly Savings: $30,814

## Slide 27
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
BREADTH STUDY: STRUCTURAL
1
1
2
2
3
3

## Slide 28
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
OVERALL EVALUATION
Chilled Water System Not Recommended
  Facility not large enough
  Energy requirement not high enough
  No life-cycle cost benefit
VRF System Recommended
  Contingent on CFD analysis
  Humidity Control Necessary
  Dependent on owner’s payback threshold


Solar Thermal System Recommended
  Quick payback
  Great climatic conditions
  Free energy!


## Slide 29
AGENDA
PROJECT INTRODUCTION
MECHANICAL DEPTH STUDIES
STRUCTURAL BREADTH
OVERALL EVALUATION
CONCLUSION / QUESTIONS
CONCLUSION
Special Thanks:
Ernest Health, Inc.
JBA Consulting Engineers
Jason Witterman
Kris Kalkowski
Stephen Haines
Dekker/Perich/Sabatini Architects
Bobby George
Faculty Advisor: Dr. William Bahnfleth
Faculty Member: Dr. Stephen Treado
Fellow AE Students

## Slide 30
QUESTIONS?