## Slide 1
River Vue Apartments
Laura Pica – Mechanical Option
Department of Architectural Engineering
Senior Thesis Program 2011-2012
Adviser – Stephen Treado
Color photo taken by Laura Pica August 2011
Color photo taken by Laura Pica August 2011

## Slide 2
Schedule
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses

## Slide 3
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Photo courtesy www.wikipedia.com
Photo taken by Laura Pica August 2011
Photo taken by Laura Pica August 2011
Photo courtesy: www.lonelyplanet.com

## Slide 4
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: 
 | 0.24062 | 0.30243 | 0.24911 | 0.016775 | 0.081573 | 0.1095
Chart: 
| sensible solar gain (Btu/h) | sensible glass transmission (Btu/h) | sensible wall transmission (Btu/h) | sensible lighting load (Btu/h) | Sensible People load(Btu/h) | sensible Misc equipment (Btu/h) | sensible cooling infiltration (Btu/h)
 | 2750676 | 124107 | 70653 | 108153 | 110600 | 798319 | 681
Building Loads
Project Cost Breakdown

## Slide 5
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Space | ASHRAE Outdoor Airflow (cfm) | As Designed Outdoor Airflow (cfm) | Requires Redesign
Common Corridor | 933 | 5250 | 
Stairwells | 346 | 3200 | 
Main Entry Lobby | 42 | 570 | 
Stair Lobby | 81 | 150 | 
Elect Equip Room | 48 | 0 | YES
Bsmt Machine Room | 96 | 0 | YES
Elevator Machine Room | 150 | 0 | YES
Boiler Room | 96 | 0 | YES
Fire Pump Room | 96 | 0 | YES
Generator Room | 96 | 0 | YES
Dwelling Units 2nd Floor | 1641 | 1156 | YES
Dwelling Units 3-14 Floors | 17504 | 8580 | YES
Dwelling Units 15-16 Floors | 2217 | 3107 | 
Fitness Center | 516 | 500 | YES
Retail Sales | 365 | 500 | 
Parking Garage | 2070 | 0 | YES

## Slide 6
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Monthly Utility Usage |  |  | 
Month | Electric (kW) | Gas (therms) | Water (gal)
1 | 722 | 36776 | 16
2 | 717 | 35939 | 13
3 | 722 | 26060 | 17
4 | 849 | 15040 | 104
5 | 839 | 4558 | 263
6 | 845 | 1307 | 411
7 | 846 | 46 | 509
8 | 844 | 1717 | 350
9 | 839 | 4782 | 238
10 | 842 | 17417 | 96
11 | 749 | 20845 | 83
12 | 726 | 33222 | 17
TOTAL | 9540 | 197709 | 2117
Typical High Rise Apartment |  |  |  | River Vue Apartments |  | 
occupancy sqft/person |  |  |  | occupancy sqft/person |  | 
Lo | Av | Hi |  |  |  | 
325 | 175 | 100 |  |  | 200 | 
lights watts/sqft |  |  |  | lights watts/sqft |  | 
Lo | Av | Hi |  |  |  | 
1 | 2 | 4 |  |  | 1 | 
refrigeration sqft/ton |  |  |  | refrigeration sqft/ton |  | 
Lo | Av | Hi |  |  |  | 
450 | 400 | 350 |  |  | 90 | 
supply air rate ( east-south-west) cfm/sqft |  |  |  | supply air rate ( east-south-west) cfm/sqft |  | 
Lo | Av | Hi |  |  |  | 
0.8 | 1.2 | 1.7 |  |  | 0.63 | 
supply air rate (north) cfm/sqft |  |  |  | supply air rate (north) cfm/sqft |  | 
Lo | Av | Hi |  |  |  | 
0.5 | 0.8 | 1.3 |  |  | 0.63 | 

## Slide 7
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
LOADS (Btu/h) |  |  |  |  | 
lighting | equipment | occupancy | solar | TOTAL Btu/h | TOTAL cfm
318096 | 7278258 | 352800 | 948365 | 8.90E+06 | 411922
AHU Sizing Load Calculations
Occupancy
Lighting
Equipment
Solar Gain
Chart: New Design Airflows
| outside airflow | cooling airflow | heating airflow | return airflow | exhaust airflow
original system | 4958 | 169033 | 169033 | 170629 | 6554
Base AHU | 4958 | 226819 | 226819 | 228415 | 6554
Need for energy conservation

## Slide 8
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: Occupancy Over 24 Hour Period
| 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24
N | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Chart: Natural Ventilation with Constant Air Changes
Strategy B c(t+∆t) | 0.044922 | 0.031367 | 0.024877 | 0.021154 | 0.018762 | 0.017104 | 0.015889 | 0.014962 | 0.014232 | 0.013642 | 0.013156 | 0.0095269 | 0.0092531 | 0.005933 | 0.005782 | 0.0026677 | 0.0025921 | 0.0025244 | 0.0024634 | 0.0024081 | 0.0023578 | 0.0023118 | 0.0022696 | 0.0022307 | 0.0021947 | 0.0021613 | 0.0021303 | 0.0021014 | 0.0020744 | 0.0020491 | 0.0020253 | 0.0020029 | 0.0019819 | 0.004563 | 0.0045346 | 0.0070899 | 0.0070558 | 0.009589 | 0.0095505 | 0.0095139 | 0.0094791 | 0.0094459 | 0.0094143 | 0.009384 | 0.0093551 | 0.0093274
Chart: Demand Control Ventilation
Strategy D c(t+∆t) | 0.9965 | 3.2522 | 3.6679 | 3.8132 | 3.8805 | 3.917 | 3.939 | 3.9533 | 3.9631 | 3.9701 | 3.9753 | 3.9793 | 3.9823 | 3.9848 | 2.9868 | 2.9884 | 1.9897 | 1.9908 | 0.99182 | 0.99261 | 0.9933 | 0.9939 | 0.99442 | 0.99487 | 0.99527 | 0.99563 | 0.99595 | 0.99623 | 0.99649 | 0.99672 | 0.99693 | 0.99712 | 0.99729 | 0.99744 | 0.99759 | 0.99772 | 1.9978 | 1.9979 | 2.998 | 2.9981 | 3.9982 | 3.9983 | 3.9984 | 3.9985 | 3.9985 | 3.9986 | 3.9986 | 3.9987 | 3.9988
c(t+∆t) = c(t) * e^(-n*∆t) + (cb + (N*q)/(n*V)) * (1-e^(-n*∆t)
Demand Control Ventilation

## Slide 9
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: New Design Airflows
| outside airflow | cooling airflow | heating airflow | return airflow | exhaust airflow
original system | 4958 | 169033 | 169033 | 170629 | 6554
Base AHU | 4958 | 226819 | 226819 | 228415 | 6554
alternative 1 - AHU w/ DCV | 6197 | 179033 | 179033 | 180629 | 7793
Chart: Annual Source Energy Consumption
| Base AHU | alternative 1 - AHU w/ DCV
 | 9015303 | 7977708

## Slide 10
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
MET =1.2 and 15 cfm of outside airflow, the expected CO2 concentration will be about 0.13 percent
Contaminant Differential (Ceq) = Co + (N/Vo)
Contaminant Calculations
Vo = outdoor airflow rate per person
N = CO2 rate per person
Co = CO2 concentration outside
Assumptions:
15 cfm/person
700 ppm
1.2 MET level means N= 0.0106 cfm
Co = 400 ppm
Ceq = 1107 ppm differential

## Slide 11
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
*See final report for full descriptions of control logic and sequence of operation
Telair Ventostate 8000 series sensors
accurate within 3% and can detect 400-1250 ppm of CO2
one sensor per floor located in return air duct
Control Logic
supply air fan VFD to start when CO2 concentration reaches 1170 ppm or more
CO2 detection between 2-3 minutes

## Slide 12
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Design alternatives studied include:
Chart: Design Airflow
| Base AHU | alternative 1 - AHU w/ DCV | alternative 2 - AHU w/ economizer | alternative 3 - AHU w/ energy recovery | alternative 4 - AHU w/ 2 stages of energy recovery
design airflow (cfm) outside airflow | 4958 | 6197 | 6197 | 6197 | 6197
design airflow (cfm) cooling airflow | 226819 | 169033 | 169033 | 169033 | 169033
design airflow (cfm) heating airflow | 226819 | 169033 | 169033 | 169033 | 169033
design airflow (cfm) return airflow | 228415 | 170629 | 170629 | 170629 | 170629
design airflow (cfm) exhaust airflow | 6554 | 7793 | 169033 | 7793 | 7793
Chart: Operation at Design Capacity
Hours at 0-25% of design capacity | 1753 | 0 | 5922 | 3399 | 6120 | 1082
Hours at 26-50% of design capacity | 4081 | 2510 | 1833 | 1004 | 1797 | 5481
Hours at 51-75% of design capacity | 2706 | 5931 | 276 | 234 | 290 | 2197
Hours at 75-100% of design capacity | 230 | 319 | 0 | 0 | 0 | 0
original system | 0 | 0 | 0 | 0 | 0
Base AHU
AHU w/ DCV
AHU w/ DCV and Economizer
AHU w/ DCV and 2 Stages of Energy Recovery: Fixed Plate HX & Runaround Coil Loop
AHU w/ DCV and 1 Stage of Energy Recovery via Fixed Plate HX (OA Preconditioning)

## Slide 13
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: Energy Consumption
building energy consumption (Btu/ft^2 yr) | 1166916 | 4603472 | 3736136 | 3689087 | 3720108 | 4000728
source energy consumption (Btu/ft^2 yr) | 3499162 | 9015303 | 7977708 | 7836626 | 7953663 | 8796652
original system | 0 | 0 | 0 | 0 | 0
Chart: Annual Emissions
CO2 | 6636650 | 26181510 | 21248680 | 20981096 | 21157522 | 22753506
SO2 | 113.1202 | 446.2529 | 362.1761 | 357.6148 | 360.6219 | 387.8244
NOX | 22.736 | 89.6964 | 72.7981 | 71.881 | 328790.0022 | 77.9525
original system | 0 | 0 | 0 | 0 | 0

## Slide 14
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: 20 Year Life Cycle Cost
| Original System | Base AHU | AHU with DCV | AHU with DCV, Economizer | AHU with DCV, 1 Stage Energy Recovery | AHU with DCV, 2 Stages of Energy Recovery
20 Year LCC | 7280111.3507 | 19748985.8849 | 17063416.7552 | 16911781.3274 | 17015622.3018 | 18606471.0989
Chart: 
| Original System | Base AHU | AHU with DCV | AHU with DCV, Economizer | AHU with DCV, 1 Stage Energy Recovery | AHU with DCV, 2 Stages of Energy Recovery
Capital Cost | 485000 | 322000 | 337200 | 344200 | 346050 | 350750
Capital Cost

## Slide 15
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: 20 Year Utility Cost
| Original System | Base AHU | AHU with DCV | AHU with DCV, Economizer | AHU with DCV, 1 Stage Energy Recovery | AHU with DCV, 2 Stages of Energy Recovery
Electric | 6573414.4725 | 12069676.7432 | 11708960.9912 | 11443926.5135 | 11688185.037 | 13273331.7428
Natural Gas | 10167.466 | 7251304.4025 | 4885841.9998 | 4885725.4017 | 4849492.1697 | 4847917.7263
Chilled Water | 179139.9534 | 73615.2804 | 72624.3054 | 179139.9534 | 73105.6361 | 75682.1709
Airflow | 169,033 cfm
Coil Size | 434 tons
Total Btu/h | 8.9MBtu/h
Annual CO2 Emissions | 20,981,096 lbm/yr
Capital Cost | $363,600
20 Year Life Cycle Cost | $16.9 Million
System Selection
Occupant comfort
Reduced energy use and emissions with control strategy
Minimum ventilation requirements met
Success measured with:
AHU with DCV and Economizer

## Slide 16
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses

## Slide 17
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Size | Capacity | Throw | NC | Pressure Drop
2x12 sill grille | 62 cfm | 9.45 feet | 20 | 0.073 in wg

## Slide 18
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Available Solar Radiation
http://gerardribas.com/wp-content/uploads/2011/05/Photovoltaic-Pannles6.jpg
5500 sq. ft. of available space
Photo taken by Laura Pica August 2011
www.rredc.nrel.gov/solar_data
β | Monthly Electric Output
0 | 1.401E+18
5 | 1.389E+22
10 | 9.904E+20
15 | 4.487E+20
20 | 1.722E+20
25 | 3.564E+20
30 | 1.177E+24
35 | 1.044E+21
40 | 6.104E+20
45 | 3.497E+20

## Slide 19
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Chart: Annual Solar Radiation
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Daily Radiation | 2038 | 3903 | 5462 | 7009 | 6079 | 4311 | 4682 | 3082 | 4591 | 3811 | 1235 | 507
Monthly Radiation | 63178 | 109284 | 169322 | 210270 | 188449 | 129330 | 145142 | 95542 | 137730 | 118141 | 38285 | 15717
Average Monthly Radiation | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333 | 118365.8333
Chart: Electric Output
Daily Electric Output (W) | 35974672.5203 | 18077911.0356 | 10374704.8279 | 11622303.4029 | 11719299.6572 | 28400131.3039 | 20619908.6631 | 22237334.2887 | 11573807.0907 | 30844192.0265 | 118235.4641 | 3289.2279
Monthly Electric Output (W) | 1115214848.1283 | 506181508.9964 | 321615849.6654 | 348669102.0877 | 363298289.3724 | 852003939.1167 | 639217168.5575 | 689357362.9493 | 358788019.8129 | 956169952.8202 | 3547063.9219 | 101966.0644
Sensible solar gain reduction of 243,549 Btu/h
(10% of total sensible load)
Energy Analysis
Windows modeled with improved U-value to represent shading

## Slide 20
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Internal Shading Analysis |  |  |  |  |  | 
# Shades | volts | amps | VA | PF | Watts | Full load amps
1 | 120 | 20 | 2400 | 1 | 2400 | 12
400 | 120 | 8000 | 960000 | 1 | 960000 | 4624
# Shades | Shade (kW) requirement per year | Annual PV Array (kW) output | ∆ (PV Output-Shading Requirement) | Annual Mechanical System Requirement (kW) | Mech Syst Need - PV Power Available | 
1 | 2102.4 | 30872 | 28770 | 9491826 | 9460954 | 
 |  |  |  |  | 0 | 
400 | 840960 |  | -810088 | 9491826 | 9460954 | 0.33%
http://mechosystems.com/UrbanShade/
http://mechosystems.com/UrbanShade/

## Slide 21
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Original Photovoltaic TOTAL |  |  | $ 712,273.54
Solar Funding | PA Federal Investment Tax Credit | 30% of total installation cost | $ 213,682.06
 | West Penn Power Sustainable Energy Fund | one time grant | $ 25,000.00
 | New Photovoltaic TOTAL |  | $ 473,591.48
Photovoltaic Array Study |  |  |  |  |  | 
Date | Year | Capital | Other Mat. |  | Elect. Escalation | Elect. Value
2011 | 1 | $ 1,473,591 | $ 100 |  | 1.00 | $ 64,461
2012 | 2 | $ - | $ 100 |  | 0.96 | $ 61,883
2013 | 3 | $ - | $ 100 |  | 0.93 | $ 59,949
2014 | 4 | $ - | $ 100 |  | 0.91 | $ 58,660
2015 | 5 | $ - | $ 100 |  | 0.91 | $ 58,660
2016 | 6 | $ - | $ 100 |  | 0.90 | $ 58,015
2017 | 7 | $ - | $ 100 |  | 0.90 | $ 58,015
2018 | 8 | $ - | $ 100 |  | 0.90 | $ 58,015
2019 | 9 | $ - | $ 100 |  | 0.91 | $ 58,660
2020 | 10 | $ - | $ 100 |  | 0.92 | $ 59,304
2021 | 11 | $ - | $ 100 |  | 0.93 | $ 59,949
2022 | 12 | $ - | $ 100 |  | 0.94 | $ 60,594
2023 | 13 | $ - | $ 100 |  | 0.94 | $ 60,594
2024 | 14 | $ - | $ 100 |  | 0.94 | $ 60,594
2025 | 15 | $ - | $ 100 |  | 0.94 | $ 60,594
2026 | 16 | $ - | $ 100 |  | 0.94 | $ 60,594
2027 | 17 | $ - | $ 100 |  | 0.94 | $ 60,594
2028 | 18 | $ - | $ 100 |  | 0.94 | $ 60,594
2029 | 19 | $ - | $ 100 |  | 0.93 | $ 59,949
2030 | 20 | $ - | $ 100 |  | 0.93 | $ 59,949
 |  |  | Net Present Value |  |  | $ 953,086
simple payback period = 26.6 years

## Slide 22
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Category | Cost for Equipment & Materials | Total installation hours | Total installation days
New Mech System | $ 865,728.62 | 18306 | 763
Old Mechanical System | $ 1,371,508.55 | 24812 | 1034
Mech System Cost Difference | $ 505,779.92 savings | 6506 | 271
Category | Total Labor Cost
New Mech System | $ 15,610.64
Old Mechanical System | $ 3,323.81
Mech System Cost Difference | $ (12,286.83)

## Slide 23
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Category | Cost for Equipment & Materials | Total installation hours | Total Labor Cost
New Mech System with Photovoltaic and Shading Systems TOTAL | $ 2,578002.16 | 18911 | $ 17,128.94
Old Mechanical System | $ 1,371,508.55 | 24812 | $ 3,323.81
Overall System Difference | $ (1,206,493.62) | 5901 | $ (13,805.13)
Type of Certification | Points Range
Certified | 26-32
Silver | 33-38
Gold | 39-51
Platinum | 52-69
www.usgbc.org

## Slide 24
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
 | Original Schedule |  | 
 | Duration (days) | Start | Finish
 | 840 | 7/25/2011 | 8/31/2012
 | Adjusted Schedule | 
 | Duration | Decrease in Time
 | 640 | 24%
Project Schedule |  |  |  |  |  |  | 
 | Original Schedule |  |  |  | Adjusted Schedule |  | 
 | Duration | Start | Finish |  | Duration | Decrease in Time | 
TOTAL | 840 | 7/25/2011 | 8/31/2012 |  | 640 | 24% | 
MEP Rough In | 465 | 7/25/2011 | 2/10/2012 |  | 340 | 27% | 
MEP Finishes | 250 | 11/21/2011 | 7/27/2012 |  | 190 | 24% | 
Punch list & Inspections | 125 | 2/27/2012 | 8/31/2012 |  | 110 | 12% | 

## Slide 25
Conclusions
Schedule
Laura Pica – Mechanical Option - Adviser – Stephen Treado
Building Overview
Existing Mechanical System
Mechanical Depth Design
Demand Control Ventilation
Mechanical Design Alternatives
Breadth 1 – Photovoltaic Array Study
Breadth 2 – CM Study
Conclusions
Acknowledgements
Energy & Cost Analyses
Photovoltaic array and internal shading not recommended
Decreased construction schedule
Increased occupant comfort
Minimum ventilation requirements met
Photo taken by Laura Pica August 2011
Next Analysis – the use of solar thermal collectors and storage to assist existing system
Recommended larger AHU with Demand Control Ventilation
Decreased capital cost

## Slide 26
My adviser, Stephen Treado, for his help in editing my technical reports and providing professional consulting
All other Department of Architectural Engineering faculty for their passion for teaching, continued support and encouragement
All AE Mentors and Practitioners from the “Mentoring Center” for their valuable design advice
Kevin Ludwick, Turner Project Manager for supplying design documents and construction data
And most importantly, my friends and family for their support throughout my senior year. I could have never finished this project without you!
Acknowledgements

## Slide 27
Thank You
Questions?

## Slide 28
Appendix

## Slide 29
Mechanical Depth Design
LOADS (Btu/h) |  |  |  |  | 
lighting | equipment | occupancy | solar | TOTAL Btu/h | TOTAL cfm
318096 | 7278258 | 352800 | 948365 | 8.90E+06 | 411922
Room No | Space Type | Area (Az) | OA Rate per person (Rp) | OA Rate (cfm) | OA Rate (cfm) | (CFM) | Btu/h
B-10 | lobby | 100 | 5 | 25 | 6 | 31 | 1.435
Room No | Space Type | Area (Az) | (Watts) | Density (W/sqft) | Btu/h
B-10 | lobby | 100 | 256 | 2.560 | 874
Equipment | Quantity | BTU/h per unit | Watts per unit |  | TOTAL Btu/h
dishwasher | 199 | 800 | 234 |  | 159200
Room No | Space Type | Expected # of occupants | occupant load (Btu/h) | CFM
B-10 | lobby | 5 | 1750 | 81
Load Calculations

## Slide 30
Breadth 2 – CM Study
Category | Equipment | Quantity | Cost Per Item (Inc. O&P) | Total Cost
Mechanical System Design Alternative | AHU – VAV for 100,000 cfm, not incl duct & accessories | 2 | $ 161,000.00 | $ 322,000.00
 | DCV Direct-Digital CO2 Detector System, incl panel & sensor | 1 | $ 1,650.00 | $ 1,650.00
 | DCV sensor | 200 | $ 950.00 | $ 190,000.00
 | DCV Wiring (ft) | 212 | $ 50.00 | $ 10,600.00
 | Economizer Add-on | 1 | $ 25,000.00 | $ 25,000.00
 | supply duct (lb) – 20” | 16299.75 | $ 5.67 | $ 92,338.08
 | supply duct (lb) – 10” | 16268.1 | $ 2.83 | $ 45,989.92
 | return duct (lb) – 20” | 24604 | $ 5.67 | $ 139,382.37
 | supply elbows | 225 | $ 18.55 | $4173.75
 | return elbows | 255 | $ 37.00 | $9435
 | supply transitions | 60 | $35 | $2100
 | diffusers | 225 | $65.5 | $14737.5
 | modulating dampers for AHU | 2 | $161 | $322
 | TOTAL |  |  | $ 857,728.62
Category | Equipment | Crew Size | $ Per crew member | Total Labor $ | Labor Hours per unit | Total installation hours
Mechanical System Design Alternative | AHU – VAV for 100,000 cfm, not incl duct & accessories | 1 | $ 14,400.00 | $ 14,400.00 | 290 | 580
 | DCV Direct-Digital CO2 Detector System, incl panel & sensor | 2 | $ 104.00 | $ 208.00 | 2 | 2
 | DCV sensor | 2 | $ 57.00 | $ 114.00 | 1.1 | 220
 | DCV Wiring (ft) | 1 | $ 16.00 | $ 16.00 | 0.2 | 42
 | Economizer Add-on | 1 | $ 590.00 | $ 590.00 | 13 | 13
 | supply duct (lb) – 20” | 2 | $ 16.90 | $ 33.80 | 0.369 | 6015
 | supply duct (lb) – 10” | 2 | $ 4.42 | $ 8.84 | 0.1 | 1627
 | return duct (lb) – 20” | 2 | $ 16.90 | $ 33.80 | 0.369 | 9079
 | supply elbows | 2 | $ 10.00 | $ 20.00 | 0.5 | 113
 | return elbows | 2 | $ 10.00 | $ 20.00 | 0.5 | 128
 | supply transitions | 2 | $ 10.00 | $ 20.00 | 0.5 | 30
 | diffusers | 4 | $ 12.30 | $ 49.20 | 0.25 | 56
 | modulating dampers for AHU | 1 | $ 49.00 | $ 49.00 | 1 | 2
 | TOTAL |  |  | $ 15,562.64 |  | 17906
Mechanical System Takeoff

## Slide 31
Breadth 2 – CM Study
Category | Equipment | Quantity | Cost Per Item (Inc O&P) | Total Cost
Photovoltaic Array | photovoltaic panel kit | 94 | $ 6,790.91 | $ 638,345.54
 | additional wiring (ft) | 212 | $ 140.00 | $ 29,680.00
 | conduit | 212 | $ 44.00 | $ 9,328.00
 | conduit cutting/drilling | 64 | $ 200.00 | $ 12,800.00
 | grounding electrode | 1 | $ 120.00 | $ 120.00
 | circiut breaker | 1 | $ 22,000.00 | $ 22,000.00
 | internal shade & motor | 400 | $ 2500 | $ 1,000,000.00
 | TOTAL |  |  | $ 1,712,273.54
Category | Equipment | Crew Size | $ Per crew member | Total Labor $ | Labor Hours per unit | Total installation hours
Photovoltaic Array | photovoltaic panel kit | 2 | $ 25.00 | $ 50.00 | 0.75 | 70.5
 | additional wiring (ft) | 2 | $ 16.00 | $ 32.00 | 1 | 212
 | conduit | 2 | $ 9.40 | $ 18.80 | 0.2 | 42.4
 | conduit cutting/drilling | 1 | $ 114.00 | $ 114.00 | 2.4 | 153.6
 | grounding electrode | 1 | $ 68.50 | $ 68.50 | 1.45 | 1.45
 | circiut breaker | 1 | $ 1,175.00 | $ 1,175.00 | 25 | 25
 | internal shade | 4 | $ 15.00 | $ 60.00 | 0.25 | 100
 | shade motor | 4 | $ 15.00 | $ 60.00 | 0.2 | 80
 | TOTAL |  |  | $ 1,578.30 |  | 685
Electrical Takeoff

## Slide 32
Breadth 2 – CM Study
Project Schedule |  |  |  |  |  | 
 | Original Schedule |  |  |  | Adjusted Schedule | 
Zone | Duration | Start | Finish |  | Duration | Decrease in Time
TOTAL | 840 | 7/25/2011 | 8/31/2012 |  | 640 | 24%
MEP Rough In | 465 | 7/25/2011 | 2/10/2012 |  | 340 | 27%
Elevator Lobbies & Stair Towers Rough In | 100 | 8/15/2011 | 12/9/2011 |  | 85 | 
Basement and Level 1 Underground Rough In | 80 | 10/24/2011 | 2/10/2012 |  | 70 | 
Level 2, 3, 4, 5 Rough In | 60 | 7/25/2011 | 10/14/2011 |  | 40 | 
Level 6 & 7 Rough In | 30 | 8/1/2011 | 9/9/2011 |  | 15 | 
Level 8 & 9 Rough In | 30 | 8/22/2011 | 9/30/2011 |  | 15 | 
Level 10 & 11 Rough In | 30 | 9/12/2011 | 10/21/2011 |  | 15 | 
Level 12 & 13 Rough In | 30 | 10/3/2011 | 11/11/2011 |  | 15 | 
Level 14, 15 & 16 Rough In | 45 | 10/24/2011 | 12/23/2011 |  | 30 | 
Penthouse and Roof Rough In | 60 | 8/8/2011 | 10/28/2011 |  | 55 | 
MEP Finishes | 250 | 11/21/2011 | 7/27/2012 |  | 190 | 24%
Elevator Lobbies & Stair Towers | 60 | 11/21/2011 | 2/10/2012 |  | 45 | 
Basement and Level 1 Underground | 20 | 1/30/2012 | 2/24/2012 |  | 15 | 
Level 2, 3, 4, 5 | 60 | 11/28/2011 | 2/17/2012 |  | 45 | 
Level 6 & 7 | 20 | 2/27/2012 | 3/23/2012 |  | 15 | 
Level 8 & 9 | 20 | 3/19/2012 | 4/13/2012 |  | 15 | 
Level 10 & 11 | 20 | 4/30/2012 | 5/25/2012 |  | 15 | 
Level 12 & 13 | 20 | 5/28/2012 | 6/22/2012 |  | 15 | 
Level 14, 15 & 16 | 30 | 6/18/2012 | 7/27/2012 |  | 25 | 
Punch list & Inspections | 125 | 2/27/2012 | 8/31/2012 |  | 110 | 12%
Basement and Level 1, 2, 3, 4, 5 | 20 | 2/27/2012 | 3/23/2012 |  | 18 | 
Level 6 & 7 | 20 | 3/26/2012 | 4/20/2012 |  | 18 | 
Level 8 & 9 | 20 | 4/23/2012 | 5/18/2012 |  | 18 | 
Level 10 & 11 | 20 | 5/28/2012 | 6/22/2012 |  | 18 | 
Level 12 & 13 | 20 | 7/2/2012 | 7/27/2012 |  | 18 | 
Level 14, 15 & 16 | 25 | 7/30/2012 | 8/31/2012 |  | 20 | 
Schedule Changes