## Slide 1
Water Bottling Facility | Mid-Atlantic United States
Mechanical Option ¦ Spring 2013 Advised by Dr. William Bahnfleth | Justyne Neborak

## Slide 2: Introduction
Water Bottling Facility
  Production
  Warehouse
  Office
Mid Atlantic Region
30 ft Ceiling Warehouse
23 ft 6 in Draft Curtain Production
8 – 30 ft Ceiling Office
Introduction

## Slide 3: Introduction
Outdoor Design Conditions
Indoor Design Conditions
 | Summer Design Cooling (0.4%) | Winter Design Heating (99.6%)
OA Dry Bulb (°F) | 88°F | 5°F
OA Wet Bulb (°F) | 72°F | -
 | Conditioned Process | Offices, QC Lab, & Parts Office | Warehouse & Packaging | Storage, Maintenance & Mechanical
Cooling Set Point | 85°F | 72°F | 95°F | 95°F
Heating Set Point | 65°F | 72°F | 48°F | 60°F
Relative Humidity | - | 45% | - | -
Introduction

## Slide 4: Existing Mechanical Systems
Heating Water System
  Only used for Manufacturing Purposes
Chilled Water System
  3 Ammonia Chillers
  4 Cooling Towers
Air Side
  5 Air Handing Units
  17 VAV Terminal Units
  8 Makeup Units
Space | Max Cooling Dry Bulb | Cooling Dew Point/Max | Relative Humidity | Min Heating Temperature
Warehouse | 80°± 2°F | 48°F/50°F | - | 60°F
Shipping Office | 74°F | - | 45% | 68°F
Main Office | 74°F | - | 45% | 68°F
Production | 80°± 2°F | 48°F/50°F | - | 60°F
Maintenance | 104°± 2°F | - | 45% | 60°F
QC Lab | 75°F | 59°F/64°F | - | 68°F
H-3 Essence | 80°± 2°F | 48°F/50°F | - | 50°F
Mechanical | 80°± 2°F | 48°F/50°F | - | 60°F
Existing Mechanical System

## Slide 5: Existing Mechanical Systems
 | Warehouse |  | Shipping office |  | Main Office
 | Production Area |  | Maintenance |  | Quality Control Lab
 | H-3 Essence |  | Mechanical Rooms |  | 
Existing Mechanical System

## Slide 6: Existing Mechanical System
Chart: Monthly Cooling Load
| January | February | March | April | May | June | July | August | September | October | November | December
 | 143.5684 | 334.9929 | 10145.4983 | 310921.2369 | 2032066.7325 | 2898358.2871 | 4557386.5339 | 4392043.6258 | 2127156.8506 | 804796.4354 | 296085.8385 | 95.7122
Chart: 
| Electrical Equipment | Lighting | HVAC
Sales | 64583837 | 12686111 | 27354233
Existing Mechanical System

## Slide 7: Existing Mechanical System
Function | Energy (kW) | Total Energy (%)
HVAC | 27,354,233 | 28.1
Lighting | 12,686,111 | 12.1
Electrical Equipment | 64,583,837 | 61.7
Chart: Electrical Cost by Use
| January | February | March | April | May | June | July | August | September | October | November | December
Equipment | 398185.7143 | 359650.4464 | 398185.7143 | 385340.625 | 398185.7143 | 385340.625 | 398185.7143 | 398185.7143 | 385340.625 | 398185.7143 | 385340.625 | 398185.7143
Lighting | 97334.2857 | 87914.5536 | 97334.2857 | 94194.375 | 97334.2857 | 94194.375 | 97334.2857 | 97334.2857 | 94194.375 | 97334.2857 | 94194.375 | 97334.2857
HVAC | 171780 | 155296 | 172535 | 168244 | 176990 | 172994 | 180518 | 180439 | 171640 | 175120 | 167917 | 171956
Existing Mechanical System

## Slide 8: Ground Coupled Heat Pump
Pipe Sizing
  6” Diameter Bores
  1” Diameter U-Tube
Bore Fill
  15% Bentonite, 85% SiO2
Ground Coupled Heat Pump
Vertical Layout
  Pros
    Less Space
    Maintains Thermal Properties of Ground
    Less Pipe
    Less Pump Energy
  Cons
    Expensive
    Specialized equipment

## Slide 9: Ground Coupled Heat Pump
 | Short-Circuit Heat Loss Factor
 | Part-Load Factor during Design Month
 | Net Annual Average Heat Transfer to Ground
 | Building Design Block Load
, | Effective Thermal Resistance of Ground
 | Thermal Resistance of Bore
 | Undisturbed Ground Temperature
 | Temperature Penalty for Interference of Adjacent Bores
, | Liquid Temperature at Heat Pump
 | System Power Input at Design Load
 | Short-Circuit Heat Loss Factor
 | Part-Load Factor during Design Month
 | Net Annual Average Heat Transfer to Ground
 | Building Design Block Load
 | Effective Thermal Resistance of Ground
 | Thermal Resistance of Bore
 | Undisturbed Ground Temperature
 | Temperature Penalty for Interference of Adjacent Bores
 | Liquid Temperature at Heat Pump
 | System Power Input at Design Load
Ground Coupled Heat Pump

## Slide 10: Ground Coupled Heat Pump
Short-Circuit Heat Loss Factor,
  1 bore/loop + 3 gpm/loop = 1.04 short-circuit heat loss factor
Part-Load Factor during Design Month,
  Unknown therefore use maximum of 1.0
Building Design Block Load, (Cooling), (Heating)
  Found using block load analysis, 6,125,519 Btu/hr & 0 Btu/hr
Net Annual Average Heat Transfer to Ground,
  Difference between heating and cooling, 6,125,519 Btu/hr
Ground Coupled Heat Pump
Undisturbed Ground Temperature,
Average Ground Temperature
53°

## Slide 11: Ground Coupled Heat Pump
Time Pulse | Fourier Number | G-Factor | Thermal Resistance (ft·h·°F/Btu)
Annual | 67,716.6 | 0.94 | 0.211
Monthly | 556.6 | 0.56 | 0.183
Daily Peak | 4.6 | 0.22 | 0.122
Effective Thermal Resistance of Ground, (Annual), (Daily), (Monthly)
  Calculate Fourier number
  Use table to find G-Factor
  Calculate Thermal Resistance
Ground Coupled Heat Pump
Rock Type | Dry Density (lb/ft3) | Conductivity (Btu/h·ft·°F) | Diffusivity (ft2/day)
Limestone | 150 to 175 | 1.4 to 2.2 | 0.9 to 1.4
Average Value | 162.5 | 1.8 | 1.15

## Slide 12: Ground Coupled Heat Pump
Thermal Resistance of Bore,
  15% Bentonite 85% SiO2, 0.10 Btu/h·ft·°F
Temperature Penalty for Interference of Adjacent Bores,
  20 ft spacing results in a penalty of 1.8°F
System Power Input at Design Load, (Cooling), (Heating)
  Based on pump selection, 112,000 W
Liquid Temperature at Heat Pump, (Inlet), (Outlet)
  Inlet 20 to 30°F higher for heating, 10 to 20°F lower for cooling
    68°F Cooling
    38°F Heating
  Outlet 10°F increase from inlet
    78°FCooling
    48°F Heating
Ground Coupled Heat Pump

## Slide 13: Ground Coupled Heat Pump
Ground Coupled Heat Pump
Variable | Cooling Value | Heating Value | Units
 | 1.04 |  | -
 | 1.0 |  | -
 | 6,125,519 |  | Btu/h
 | 6,125,519 | 0 | Btu/h
 | 0.211 |  | ft·h·°F/Btu
 | 0.183 |  | ft·h·°F/Btu
 | 0.122 |  | ft·h·°F/Btu
 | 0.10 |  | ft·h·°F/Btu
 | 53 |  | °F
 | 1.8 |  | °F
 | 78 | 38 | °F
 | 88 | 48 | °F
 | 112,000 | 112,000 | W
 | 125,020 | 0 | ft
Variable | Cooling Value | Heating Value | Units
 | 1.04 |  | -
 | 1.0 |  | -
 | 6,125,519 |  | Btu/h
 | 6,125,519 | 0 | Btu/h
 | 0.211 |  | ft·h·°F/Btu
 | 0.183 |  | ft·h·°F/Btu
 | 0.122 |  | ft·h·°F/Btu
 | 0.10 |  | ft·h·°F/Btu
 | 53 |  | °F
 | 1.8 |  | °F
 | 78 | 38 | °F
 | 88 | 48 | °F
 | 112,000 | 112,000 | W
 | 125,020 | 0 | ft

## Slide 14: Ground Coupled Heat Pump
 | Length (ft) | Multiplicity | Total Length (ft) | Head Loss (ft/100 ft) | Total Head Loss (ft)
Bore | 400 | 2 | 800 | 2.5 | 20
Longest Branch | 20 | 60 | 1200 | 2.5 | 30
Tee-Fittings | 7 | 2 | 14 | 2.5 | 0.35
Elbows | 3.5 | 4 | 14 | 2.5 | 0.35
Total |  |  |  |  | 50.7
Ground Coupled Heat Pump
Head Loss Calculations
 | Length (ft) | Flow Rate (gpm) | Fittings | Equivalent Length (ft) | Head Loss (ft/100ft) | Total Head Loss (ft)
Header | 2800 | 1531 | 6 90° elbows | 66 | 3.5 | 100.31
1 | 100 | 1505 | 2 Tees | 14 | 3.5 | 3.99
2 | 100 | 1480 | 2 Tees | 14 | 3.5 | 3.99
3 | 100 | 1455 | 2 Tees | 14 | 3.5 | 3.99
4 | 100 | 1430 | 2 Tees | 14 | 3.5 | 3.99
5 | 100 | 1405 | 2 Tees | 14 | 3 | 3.42
6 | 100 | 1380 | 2 Tees | 14 | 2.5 | 2.85
⁞ | ⁞ | ⁞ | ⁞ | ⁞ | ⁞ | ⁞
60 | 100 | 25 | 2 Tees | 14 | 0.7 | 0.798
Total |  |  |  |  |  | 203.252

## Slide 15: Ground Coupled Heat Pump
Pump
Heat Pump
21 Rooftop Units
  Twenty 25 ton
  One 10 ton
Ground Coupled Heat Pump
Manufacturer | Bell & Gossett
Model | 4x6x10M HSC3
Flow Rate (gpm) | 1531
Head (ft) | 254
Impeller Diameter (in) | 8.3
RPM | 3565
HP | 150

## Slide 16: Cost Analysis
Cost Analysis
Month | Original Energy (kWh) | GCHP Energy (kWh) | Difference (kWh)
January | 2,275,032 | 1,713,184 | 561,848
February | 2,056,716 | 1,547,770 | 508,946
March | 2,285,022 | 1,707,854 | 577,168
April | 2,228,204 | 1,654,628 | 573,576
May | 2,344,024 | 1,729,509 | 614,515
June | 2,291,104 | 1,690,252 | 600,852
July | 2,390,752 | 1,765,344 | 625,408
August | 2,389,709 | 1,764,376 | 625,333
September | 2,273,169 | 1,677,335 | 595,834
October | 2,319,265 | 1,715,919 | 603,346
November | 2,223,874 | 1,655,288 | 568,586
December | 2,277,362 | 1,712,482 | 564,880
Largest Difference |  |  | 116,462
Average Value |  |  | 585,024
Chart: Monthly Energy Use
| January | February | March | April | May | June | July | August | September | October | November | December
Original | 2275032 | 2056716 | 2285022 | 2228204 | 2344024 | 2291104 | 2390752 | 2389709 | 2273169 | 2319265 | 2223874 | 2277362
GCHP | 1713183.7307 | 1547769.986 | 1707854.1374 | 1654628.331 | 1729509.1164 | 1690252.4544 | 1765343.6185 | 1764375.8766 | 1677335.2034 | 1715918.6536 | 1655287.5175 | 1712482.4684

## Slide 17: Cost Analysis
Design | Energy Usage (kWh) | Electric Cost
Original | 27,354,230 | $ 2,065,428
Ground Source Heat Pump | 19,201,080 | $ 1,449,730
Difference | 8,153,150 | $ 615,698
Cost Analysis

## Slide 18: Emissions Analysis
Pollutant | Regional Grid Emission Factors 2007 (lb/kWh) | Calculated Emissions (lb/year) |  | Reduction in Emissions
 |  | Original | GCHP | 
CO2e | 1.74E+00 | 3.96E+06 | 2.98E+06 | 25%
CO2 | 1.64E+00 | 3.37E+06 | 2.54E+06 | 25%
CH4 | 3.59E-03 | 8.20E+03 | 6.13E+03 | 25%
N2O | 3.87E-05 | 8.62E+01 | 6.40E+01 | 26%
NOX | 3.00E-03 | 7.03E+03 | 5.19E+03 | 26%
SOX | 8.57E-03 | 1.96E+04 | 1.45E+04 | 26%
CO | 8.54E-04 | 2.04E+03 | 1.51E+03 | 26%
TNMOC | 7.26E-05 | 1.73E+02 | 1.28E+02 | 26%
Lead | 1.39E-07 | 3.16E-01 | 2.33E-01 | 26%
Mercury | 3.36E-08 | 7.79E-02 | 5.77E-02 | 26%
PM10 | 9.26E-05 | 2.06E+02 | 1.53E+02 | 26%
Solid Waste | 2.05E-01 | 4.67E+05 | 3.51E+05 | 25%
Emissions Analysis

## Slide 19: Photovoltaic Design
Chart: Global Horizontal Radiation
| January | February | March | April | May | June | July | August | September | October | November | December
Daily Radiation | 1885.5152 | 2701.2856 | 3797.0316 | 4928.5333 | 5517.4515 | 5814.6662 | 5971.9013 | 5154.0637 | 4170.1317 | 3119.904 | 1911.5676 | 1602.2901
Monthly Radiation | 58450.9723 | 75635.9965 | 117707.9792 | 147855.999 | 171040.9959 | 174439.9869 | 185128.9394 | 159775.9751 | 125103.951 | 96717.0249 | 57347.0289 | 49670.9931
33°
25°
Photovoltaic Design

## Slide 20: Photovoltaic Design
Panel Length | Panel Width | Array Tilt Angle | Height From Ground | Horizontal Length | Distance Between Panels | Row Spacing
39.1 in | 77.6 in | 33° | 21.3 in | 32.8 in | 63.9 in | 96.7 in
Sharp ND-F4Q300 Electrical Characteristics | 
Maximum Power (Pmax) | 300 W
Open Circuit Voltage (Voc) | 45.1 V
Maximum Power Voltage (Vpm) | 35.2 V
Short Circuit Current (Isc) | 8.94 A
Maximum Power Current (Ipm) | 8.52 A
Module Efficiency (%) | 15.3%
Maximum System (DC) Voltage | 1000 V
Temperature Coefficient (Pmax) | -0.439%/°C
Temperature Coefficient (Voc) | -0.321%/°C
Temperature Coefficient (Isc) | 0.050%/°C
h
h
Photovoltaic Design

## Slide 21: Photovoltaic Design
Month | Beam Incident Radiation (kWh/m2) | Total Incident Radiation (kWh/m2) | Net DC Output (kWh) | Net AC Output (kWh)
January | 55.95 | 90.61 | 50,402 | 41,602
February | 50.55 | 97.46 | 84,698 | 75,567
March | 76.06 | 134.88 | 154,112 | 142,010
April | 79.07 | 146.97 | 226,988 | 212,703
May | 77.37 | 153.18 | 274,686 | 258,784
June | 69.07 | 151.30 | 275,015 | 259,367
July | 83.74 | 163.15 | 295,087 | 278,953
August | 80.86 | 152.08 | 237,668 | 223,063
September | 74.28 | 134.93 | 165,337 | 153,409
October | 76.37 | 124.04 | 93,685 | 83,602
November | 43.55 | 80.11 | 55,004 | 46,542
December | 50.17 | 79.11 | 42,569 | 34,245
Photovoltaic Design

## Slide 22: Photovoltaic Design
Payback Period
  Infinite
 | # of units | kW/unit | kW | $/W | Total
Module | 7695 | 0.3 | 2307.76 | 2.05 | $ 4,730,910.62
Inverter | 5 | 500 | 2500 | 0.37 | $ 925,000.00
Balancing | - | - | - | 0.43 | $ 992,337.3
Installation Labor | - | - | - | 0.48 | $ 1,107,725.41
Margin And Overhead | - | - | - | 0.81 | $ 1,869,286.64
Permitting | - | - | - | 0.23 | $ 530,785.09
Grid Interconnection | - | - | - | 0.01 | $ 23,077.61
Total |  |  |  | $ 4.62 | $ 10,660,385.73
Photovoltaic Design

## Slide 23: Acoustical Design
Duration Per Day (h) | Sound Level (dBA)
8 | 90
6 | 92
4 | 95
3 | 97
2 | 100
1 ½ | 102
1 | 105
½ | 110
¼ or less | 115
Chart: Extrapolation of OSHA Standard
| 8 | 6 | 4 | 3 | 2 | 1.5 | 1 | 0.5 | 0.25 | 12
 | 90 | 92 | 95 | 97 | 100 | 102 | 105 | 110 | 115 | 87.029
Acoustical Design

## Slide 24: Acoustical Design
 | SL < 87 dBA
 | 87dBA ≤ SL <90 dBA
 | SL ≥ 90 dBA
80
70
86
87
86
86
87
89
101
72
93
92
89
96
85
87
89
89
88
86
85
82
87
91
87
87
91
89
91
88
90
90
90
91
87
88
76
80
90
91
73
79
81
83
81
80
80
88
88
84
90
89
89
89
87
87
91
86
86
84
85
89
88
77
81
81
Acoustical Design

## Slide 25: Acoustical Design
Step 1: Determine Surface Area
Step 2: Determine Overall Acoustical Character
Surface | Acoustical Characteristic
Walls: | Hard x 5 (Concrete) Medium x 1 (Stacked Pallets)
Floor: | Hard (Concrete)
Ceiling: | Hard (Steel)
Combined Characteristic: | Medium Hard
Surface | Dimensions (ft) | Number of Surfaces | Area (ft2)
Walls | 23.5 x 315 23.5 x 439 | 2 2 | 14,805 20,633
Floor | 315 x 439 | 1 | 138,285
Ceiling | 315 x 439 | 1 | 138,285
Total |  |  | 312,008
Acoustical Design

## Slide 26: Acoustical Design
Steps 3-5: Plot Information from Previous Steps on Nomogram
Quality | Results
Room Surface Area (ft2) | 312,008
Average Room Absorption Coefficient | Medium Hard
dB Reduction (dBA) | 10
Number of Baffles Required | 6,000
Acoustical Design

## Slide 27: Acoustical Design
Acoustical Design

## Slide 28: Conclusion
Ground Coupled Heat Pump
  Save Money
  Reduce Emissions
Photovoltaics
  Not Feasible
Acoustics
  Able to reduce the Sound Level by 10 dBA
Conclusion

## Slide 29: Acknowledgements
Thank You!
AE Professors, Advisors, & Staff
The Water Bottling Facility
Jack, Ron, & Chris
My Parents & Family
My Friends & Classmates
Conclusion

## Slide 30: References
"Copper Roof Vents and Steel Roof Caps for Exhaust by Luxury Metals." Copper Roof Vents and Steel Roof Caps for Exhaust by Luxury Metals. 03 Mar. 2013 <http://www.luxurymetals.com/roofcaps.html>.
Deru, M. and P Torcellini, Source Energy and Emission Factors for Energy Use in Buildings. Technical Report NREL/TP-550-38617
"Energy.gov." Geothermal Heat Pumps. N.p., 24 June 2012. Web. 17 Dec. 2012.
"Geothermal Heating Contractor for Massachusetts and surrounding area." Geothermal Heating Contractor for Massachusetts and surrounding area. 03 Mar. 2013 <http://www.geosundesign.com/Deep_Earth_Temperature_Map.html>.
"Index of /images/Geologic." Index of /images/Geologic. 03 Mar. 2013 <http://mapagents.com/images/Geologic/>.
McDowall, Robert, and Ross Montgomery. Fundamentals of HVAC control systems. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers, 2011.
"Occupational Noise Exposure - 1910.95." OSHA.gov. OSHA, n.d. Web. 17 Dec. 2012.
"PA DCNR Map Viewer." PA DCNR Map Viewer. 03 Mar. 2013 <http://www.gis.dcnr.state.pa.us/maps/index.html?geology=true>.
"Pump manufacturer representatives, commercial pumps, residential pumps, submersible pumps, circulators, heating pumps, chiller pumps, condenser pumps." 04 Mar. 2013 <http://bell-gossett.com/pumpsbg.htm>.
"Rooftop WSHP." DX Unitary HVAC System. 04 Mar. 2013 <http://www.trane.com/COMMERCIAL/Dna/View.aspx?i=1122>.
"Solar PV Tilt Angle Graph." PV System Tilt Angle Graph. 09 Apr. 2013 <http://www.mrsolar.com/content/pv_tilt_angle.php>.
Haskel Architects and Engineers Engineering Reports
Water Bottling Facility Specifications and Images
Conclusion

## Slide 31: Questions?
Conclusion