## Slide 1
The State Institute of Rehabilitation
New Jersey
Elizabeth C. Krauss
Mechanical Option

## Slide 2
The State Institute of Rehabilitation
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 3
Outdoor Conditions
  Summer (0.4%):
    94oF DB
    74.9oF WB
  Winter (99.6%):
    11oF DB
Indoor Conditions
  Summer:
    75oF DB
    50% RH
  Winter:
    72oF DB
    50% RH
  Location
  Occupancy
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 4
  Facility
  Façade
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 5
  Heating
  Cooling
Boiler-1(1973):
Natural Gas
Output: 5021 MBH
Boiler-2(1973):
Natural Gas
Output: 5021 MBH
Chiller-1(1973):
Electric Centrifugal
Output: 300 tons
Chiller-2(1973):
Air Cooled Liquid
Output: 15.2 tons
Chiller-2(1973):
Air Cooled Liquid
Output: 18.4 tons
Decommissioned Chiller (1973):
Steam Absorption
Output: 230 tons
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 6
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
RTU-1
39 Tons cooling
470 MBH heating
11500 CFM
  Rooftop Units
  Capacities
Total:
381 Tons cooling | 4516 MBH | 112,500 CFM
RTU-2
39 Tons cooling
470 MBH heating
11500 CFM
RTU-3
45 Tons cooling
470 MBH heating
12000 CFM
RTU-4
45 Tons cooling
470 MBH heating
12000 CFM
RTU-5
47 Tons cooling
570 MBH heating
14000 CFM
RTU-6
47 Tons cooling
570 MBH heating
14000 CFM
RTU-7
40 Tons cooling
510 MBH heating
12500 CFM
RTU-8
39 Tons cooling
510 MBH heating
12500 CFM
RTU-9
39 Tons cooling
476 MBH heating
12500 CFM

## Slide 7
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Heating
  Equipment
Boilers-1
Input: 2000 MBH
Output: 1600 MBH
Boilers-2
Input: 2000 MBH
Output: 1600 MBH
Boilers-3
Input: 2000 MBH
Output: 1600 MBH
8 Cabinet Unit Heaters
8 Unit Heaters
137 Variable Air Volume Units, hot water reheat

## Slide 8
  Building Addition, Electricity
  Existing Building, Electricity
= 1890 MWh
=(2)*1890 MWh
= 3780 MWh
Total: 5,671 MWh
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 9
  Operation Cost, Building Addition
  Operation Cost, Existing Building
(134,861) + (120,226)
=$255,087
(269,772) + (240,452)
=$510,174
Building Summary
  Location and Occupancy
  Facility and Façade
  Equipment
    Existing Building
    Building Addition
  Electric Consumption
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 10
  Objectives
Upgrade
Increase
Decrease
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Plan
Combined Heat, Cooling, and Power
Source: United States Environmental Protection Agency (EPA)

## Slide 11
  Heating
  Boilers
Peak Demand Loads
Existing Building
2 * (5021 MBH)
= 10042 MBH
Building Addition
4080 MBH
Total:
10042 MBH
+ 4080 MBH
14,122 MBH Demand
14,122 MBH ÷ (3 boilers) = 4703.3 MBH/boiler
(3) 6400 MBH Output
(3) 8000 MBH Input
6,598 lbs./hr. steam ea.
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 12
  Waste Heat
  Combustion Turbine
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 13
  Cooling Loads
  Double Effect Absorption Chiller
Peak Demand Loads
Existing Building
300 tons
+ 18.4 tons
+ 15.2 tons
= 333.6 tons
Building Addition
448 tons
Total:
333.6 tons
+448.0 tons
781.6 ton Demand
802 ton capacity
6873 lbs. steam/hr. consumption
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 14
  Air Distribution, Addition
Cooling:
DX to Chilled Water
Heating:
Gas Burner to Steam
  Air Distribution, Existing
Cooling:
Chilled Water
Heating:
Steam
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 15
  Operation, Winter
1.2 MW electricity
  Operation, Summer
6745 MBH Waste Heat
6400 MBH, 6598 lbs. steam
1255 MBH Nat. Gas
8000 MBH Nat. Gas
8000 MBH Nat. Gas
1.2 MW electricity
6745 MBH Waste Heat
6598 lbs./hr. steam
1255 MBH Nat. Gas
802 tons cooling
6400 MBH, 6598 lbs. steam
6400 MBH, 6598 lbs. steam
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 16
  Building Addition, Demand
  Existing Building, Demand
Maximum Heating Load: 7,471,248,000 BTU, Jan.
Maximum Cooling Load: 2,978,380,800 BTU, July
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 17
  Annual Operating Cost
  Annual Operating Cost, Cooling
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 18
  Emissions, Before
  Emissions, After
Electricity
Natural Gas
Total
29,211,537 lbs. CO2 | 8,213 lbs. SO2 | 44,912 lbs. NO
Natural Gas
Total
46,671,200 lbs. CO2 | 4,112 lbs. SO2 | 69,904 lbs. NO
Electricity
37% increase CO2 | 50% decrease lbs. SO2 | 35% increase NO
0
Building Summary
Objectives
Mechanical Investigation
  Equipment
    Boilers
    Combustion Turbine
    Chiller
    Air Distribution
  Operations and Cost
  Emissions
Electrical Investigation
Overall Evaluation
Conclusion

## Slide 19
  First Cost, System
  Incentives
Electricity
$1,882,780.00-$620,000.000 = $1,262,780
32.9% savings
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
  First Cost & Offset
  Cost of Operation & Grid Resale
Overall Evaluation
Conclusion

## Slide 20
  Grid Resale
=$340,981 earned
  Costs of Operation
Before Retrofit
(255,087, Addition)+(510,174, Existing) = $765,261
After Retrofit
(458,418, boilers)+(371,945,CT) = $830,364
$830,364-$340,981 = $489,383
36% decrease in operational costs
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
  First Cost & Offset
  Cost of Operation & Grid Resale
Overall Evaluation
Conclusion

## Slide 21
  Equipment
Installed Equipment
(1) Gas-fired generator Combustion Turbine (1.2 MW)
Altered Equipment
Rooftop Air Handling Units
DX to Chilled Water
Gas Burner to Steam
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
(1) 6400 MBh waste-heat fueled, forced draft steam boiler
(2) 6400 natural-gas fired, forced draft steam boilers
(1) 802 ton steam absorption chiller
  Performance
37% increase CO2 | 50% decrease lbs. SO2 | 35% increase NO
32.9% first-cost savings
36% decrease in operational costs

## Slide 22
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
Acknowledgements
Thank you to:
Robert Gould P.E.
Dr. Laura Miller
Also to:
Family
Friends
Fellow AE students

## Slide 23
Questions

## Slide 24
  Mechanical Space, Before
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Mechanical Space
  Domestic Water Reheat
  Electricity Production, Plant vs. Site
  Mechanical Space, After

## Slide 25
  Domestic Water Reheat
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Mechanical Space
  Domestic Water Reheat
  Electricity Production, Plant vs. Site
  Inputs

## Slide 26
  Results
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Mechanical Space
  Domestic Water Reheat
  Electricity Production, Plant vs. Site
8.088 MBh heat recovered
358.87 MBh required
2.3% savings
Suggestions
Change condensate pipe to copper
Increase length of apparatus
Duplicate apparatus for existing building sanitary line

## Slide 27
  1.2 MW Electricity, Plant
Electricity, Consumed
Total
16,511,351 lbs. CO2 | 11,909 lbs. SO2 | 26,879 lbs. NO
Total
20,905,565 lbs. CO2 | 1,842 lbs. SO2 | 31,312 lbs. NO
21% increase CO2 | 84% decrease lbs. SO2 | 14% decrease NO
  1.2 MW Electricity, Site
Electricity, Produced
Building Summary
Objectives
Mechanical Investigation
Electrical Investigation
Overall Evaluation
Conclusion
  Mechanical Space
  Domestic Water Reheat
  Electricity Production, Plant vs. Site