## Slide 1
Dan Hanley
Architectural Engineering Senior Thesis Presentation
Pennsylvania State University
Mechanical Option
North Pocono High School
Building System Integration
Energy and Cost Analysis

## Slide 2
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1
Mechanical System Redesign
Redesign Objectives
Sizing the Ground Loop
Ground Source Heat Pump
Dedicated Outdoor Air System
System Comparison
Energy Comparison
Cost Comparison
Environmental Comparison
Structural Breadth
Load Comparison
Member Comparison
Cost Comparison
Electrical Breadth

## Slide 3
North Pocono High School
Dan Hanley
Mechanical Option
Project Outline
Project Location:
Covington Township, PA
Delivery Method:
Design – Bid – Build
Design Base Bid:
$30 Million
Construction Dates:
July 2007 – Sept. 2009
Project Size:
3 Levels
230,000 ft2

## Slide 4
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Criteria
Air Side System
Hydronic System

## Slide 5
North Pocono High School
Dan Hanley
Mechanical Option
Existing Conditions
Design Criteria:
Restrained by Budget
Follow the 2005 International Mechanical Code
Design Conditions:
Latitude | 41.14o
Longitude | 75.52o
Elevation | 550 ft
Cooling Design DBT | 87 oF
Heating Design DBT | 5 oF
Cooling DBT | 72 oF
Heating DBT | 72 oF
Relative Humidity | 50 %
Outdoor Design Conditions
Indoor Design Conditions

## Slide 6
North Pocono High School
Dan Hanley
Mechanical Option
Existing Conditions
Air Side System
16 Direct Expansion Rooftop Air Handlers
12 VAV AHU with Duct Mounted Hot Water Coils
100 VAV Box Reheat Coils

## Slide 7
North Pocono High School
Dan Hanley
Mechanical Option
Existing Conditions
Air Side System
16 Direct Expansion Rooftop Air Handlers
4 CV AHU with Hot Water Coils
Condition: Auditorium
2 – Multi-Use Space
Locker Room Area

## Slide 8
North Pocono High School
Dan Hanley
Mechanical Option
Existing Conditions
Hydronic System
2 – 7,000 MBH Oil Fired Boilers
Heating Coils in the AHU
Reheat Coils in the VAV Terminal Units
Boiler 2
Boiler 1
Expansion Tanks
Air Separator
Pumps
Chemical
Treatment
Return
Water
Supply
Water

## Slide 9
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1

## Slide 10
North Pocono High School
Dan Hanley
Mechanical Option
ASHRAE Standards
ASHRAE Standard 90.1
Building Envelope
Fenestration is <40% of Total Enclosure
Element | Insulation R-Value | Standard Min. R-Value | Compliant | Assembly U-Value | Assembly Max. U-Value | Compliant
Roof | 10 | 20 | No | 0.681 | 0.48 | No
Wall Type 1 | 10 | 11.4 | No | 0.67 | 0.09 | Yes
Wall Type 2 | 10 | 11.4 | No | 0.093 | 0.09 | No
Slab on Grade | NR | NR | NR | 0.213 | 0.73 | Yes
Fenestration | Assembly U-Value | Assembly Max. U-Value | Assembly SHGC | Max SHGC | Compliant
Metal Framing | 0.5 | 0.45 | 0.55 | 0.4 | No
Opaque Surfaces
Fenestration

## Slide 11
North Pocono High School
Dan Hanley
Mechanical Option
ASHRAE Standards
ASHRAE Standard 90.1
Building Equipment
Building Area >25,000 ft2
Unit | Air Flow (cfm) | CFM*0.0015 | Fan HP | Complaint
AHU-1 | 15,850 | 23.8 | 25 | No
AHU-2 | 16,415 | 24.6 | 25 | No
AHU-3 | 36,000 | 54.0 | 25 | Yes
AHU-4 | 3,700 | 5.6 | 5 | Yes
AHU-5 | 6,800 | 10.2 | 15 | No
AHU-6 | 19,500 | 29.3 | 20 | Yes
AHU-7 | 13,500 | 20.3 | 20 | Yes
AHU-8 | 12,650 | 19.0 | 20 | No
AHU-9 | 14,195 | 21.3 | 25 | No
AHU-10 | 8,565 | 12.8 | 15 | No
AHU-11 | 3,000 | 4.5 | 5 | No
AHU-12 | 3,800 | 5.7 | NA | NA
AHU-13 | 18,200 | 27.3 | 30 | No
AHU-14 | 10,300 | 15.5 | 10 | Yes
AHU-15 | 15,300 | 23.0 | 25 | No
AHU-16 | 3,000 | 4.5 | 5 | No
Air Handler Compliancy

## Slide 12
North Pocono High School
Dan Hanley
Mechanical Option
ASHRAE Standards
ASHRAE Standard 62.1
Label | ASHREA Standard | Designer Value
 | (cfm) | (cfm)
AHU-1 | 4,195 | 4,355
AHU-2 | 5,025 | 7,360
AHU-3 | 4,810 | 10,270
AHU-5 | 2,750 | 3,860
AHU-6 | 2,865 | 19,500
AHU-7 | 4,525 | 4,800
AHU-8 | 3,895 | 4,315
AHU-9 | 5,370 | 6,225
AHU-10 | 1,670 | 3,685
AHU-11 | 465 | 3,000
AHU-12 | 2,400 | 2,255
AHU-13 | 5,105 | 10,725
AHU-14 | 1,985 | 2,470
AHU-15 | 3,950 | 5,890
AHU-16 | 470 | 3,000
Total | 49,480 | 91,710
Difference | 42,230 | 

## Slide 13
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1
Mechanical System Redesign
Redesign Objectives
Sizing the Ground Loop
Ground Source Heat Pump
Dedicated Outdoor Air System

## Slide 14
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Redesign Objectives
Lower Energy Use
Lower Life Cycle Cost
Lower Emissions

## Slide 15
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Dedicated Outdoor Air System (DOAS)
15 DOAS Units Replaced 15 DX AHU
Saved Energy
Saved in Operating Cost
Ground Source Heat Pumps (GSHP)
Sized to Handle the Majority of the Sensible Load
3 Different Models were Selected

## Slide 16
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
DOAS
ASHRAE Standard 90.1
Unit | Air Flow (cfm) | CFM*0.0015 | Fan HP | Compliant
DOAS-1 | 4,195 | 6.3 | 5 | Yes
DOAS-2 | 4,815 | 7.2 | 5 | Yes
DOAS-3 | 4,810 | 7.2 | 5 | Yes
DOAS-5 | 2,750 | 4.1 | 3 | Yes
DOAS-6 | 2,865 | 4.3 | 3 | Yes
DOAS-7 | 4,525 | 6.8 | 5 | Yes
DOAS-8 | 3,895 | 5.8 | 5 | Yes
DOAS-9 | 4,910 | 7.4 | 5 | Yes
DOAS-10 | 1,670 | 2.5 | 1.5 | Yes
DOAS-11 | 935 | 1.4 | 1 | Yes
DOAS-12 | 2,115 | 3.2 | 3 | Yes
DOAS-13 | 5,105 | 7.7 | 5 | Yes
DOAS-14 | 1,985 | 3 | 2 | Yes
DOAS-15 | 3,950 | 5.9 | 5 | Yes
DOAS Compliancy

## Slide 17
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Sizing the Ground Loop
Building Heat Gains and Losses
Hours | Heat Losses (MBh) | Heat Gains (MBh)
8 a.m. – Noon | 15186.2 | 11621.7
Noon – 4 p.m. | 15779.0 | 11133.4
4 p.m. – 8 p.m. | 851.0 | 623.2
8 p.m. – 8 a.m. | 0 | 0

## Slide 18
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Sizing the Ground Loop
Ground Properties
Piping Properties

## Slide 19
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Sizing the Ground Loop
Ground Loop Layout and Location
Vertical Closed Loop
30 rows x 35 loops with 8 bores per a loop
140,000 ft2

## Slide 20
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
Ground Loop Performance
Heating Capacity - 3,200 MBH
Heating Needed - 5,100 MBH
Boiler
Conditioned spaces
Ground Loop

## Slide 21
North Pocono High School
Dan Hanley
Mechanical Option
Dedicated Outdoor Air Ceiling Diffusers
Console Heat Pump
Typical Classroom Space
Carrier’s Console Model
Mechanical System Redesign
GSHP Selection
Classroom Spaces
Console Water Source Heat Pumps

## Slide 22
North Pocono High School
Dan Hanley
Mechanical Option
Mechanical System Redesign
GSHP Selection
Carrier’s Packaged
Heat Pump
Administrative Area
Cafeteria
Gymnasium
Auditorium
Carrier’s
Rooftop Heat Pump

## Slide 23
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1
Mechanical System Redesign
Redesign Objectives
Sizing the Ground Loop
Ground Source Heat Pump
Dedicated Outdoor Air System
System Comparison
Energy Comparison
Cost Comparison
Environmental Comparison

## Slide 24
North Pocono High School
Dan Hanley
Mechanical Option
System Comparison
Energy Comparison
Chart: Total Building Energy Total Source Energy
Current System | 15841815 | 33036914
New System | 4044143 | 12112786
Energy Consumption Per Year
75% Reduction In Building Energy
63% Reduction In Source Energy

## Slide 25
North Pocono High School
Dan Hanley
Mechanical Option
System Comparison
Cost Comparison
Initial Cost
Column1 | Cost ($)
New Mechanical Cost | 50,291,756
Original Initial Cost | 4,300,000
Difference | 45,991,756
Total Utility Cost per Year
New System Saves $187.4 Thousand
Current System – $1.30/ft2-yr
New System – $0.43/ft2-yr
Chart: Current System New System
Current System | 279972 | 92533

## Slide 26
North Pocono High School
Dan Hanley
Mechanical Option
System Comparison
Environmental Comparison
Chart: Current System New System
 | 5645226 | 1441129
Chart: SO2 NOx
Current System | 43645 | 8773
New System | 11142 | 2240
CO2 Yearly Emissions
SO2 and NOx Yearly Emissions
Total Emissions Reduced by 75%

## Slide 27
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1
Mechanical System Redesign
Redesign Objectives
Sizing the Ground Loop
Ground Source Heat Pump
Dedicated Outdoor Air System
System Comparison
Energy Comparison
Cost Comparison
Environmental Comparison
Structural Breadth
Load Comparison
Member Comparison
Cost Comparison

## Slide 28
North Pocono High School
Dan Hanley
Mechanical Option
Structural Breadth
Roof Structure
Non- Composite 1.5” 20 gauge steel deck – 7.0 psf
Supported by Steel Joists
Joists Bear on 8” CMU Walls

## Slide 29
CURRENT ROOF LOADS |  |  | REDESIGNED ROOF LOADS |  | 
Unit | Weight (lbs) | Weight (lbs/ft2) | Unit | Weight (lbs) | Weight (lbs/ft2)
AHU-1 | 8,295 | 61.4 | DOAS-1 | 4,975 | 43.7
AHU-2 | 9,360 | 32.8 | DOAS-2 | 4,975 | 43.7
AHU-3 | 23,752 | 52.8 | DOAS-3 | 5,575 | 49.0
AHU-4 | 2,816 | 33.4 | AHU-4 | 2,816 | 33.4
AHU-5 | 4,903 | 45.5 | DOAS-5 | 3,280 | 38.2
AHU-6 | 12,815 | 46.1 | DOAS-6 | 3,260 | 38.0
AHU-7 | 6,602 | 43.2 | DOAS-7 | 4,975 | 43.7
AHU-8 | 5,553 | 39.6 | DOAS-8 | 3,260 | 38.0
AHU-9 | 8,364 | 41.2 | DOAS-9 | 4,975 | 43.7
AHU-10 | 4,903 | 45.5 | DOAS-10 | 3,160 | 36.8
AHU-11 | 4,891 | 55.7 | DOAS-11 | 2,720 | 31.7
AHU-12 | 1,896 | 26.2 | DOAS-12 | 2,855 | 33.3
AHU-13 | 9,965 | 32 | DOAS-13 | 5,075 | 44.4
AHU-14 | 4,731 | 39.1 | DOAS-14 | 3,160 | 36.8
AHU-15 | 8,364 | 41.2 | DOAS-15 | 3,260 | 38.0
AHU-16 | 4,891 | 55.7 | RTG-1 (3) | 1,960 | 59.6
CU-2a | 4,057 | 43.4 | RTG-2 (2) | 1,770 | 53.9
CU-2b | 4,057 | 43.4 | x | x | x
CU-3 | 3,998 | 29.4 | x | x | x
CU-4 | 484 | 28.9 | x | x | x
CU-5 | 484 | 28.9 | x | x | x
CU-8 | 531 | 20.9 | x | x | x
Total | 135,712 | 886.3 | Totals | 62,051 | 705.9
North Pocono High School
Dan Hanley
Mechanical Option
Structural Breadth
Load Comparison
Controlling Snow Load – 39 psf
55% Reduction in Weight

## Slide 30
North Pocono High School
Dan Hanley
Mechanical Option
Structural Breadth
Equipment Location
Current Locations
Redesigned Locations

## Slide 31
North Pocono High School
Dan Hanley
Mechanical Option
Structural Breadth
Member Comparison
Section | Joist Span | Joist Spacing | Current Joist | Redesigned Joist
Section 1 | 29'- 4" | 5'-2" | 22K9 | 16K2
Section 2 | 34'-8" | 5'-8" | 24K9 | 18K3
 | 13'-1" | 5'-6" | 16KCS3 | 10K1
Section3 | 13'-0" | 5'-10 1/8" | 12K3 | 10K1
 | 34'-8" | 5'-7 1/2" | 24k9 | 26k6
 | 13'-4" | 5'-0" | 16KCS3 | 10K1
Section 4 | 38'-0" | 5'-7 1/2" | 24K9 | 28k6
 | 13'-0" | 5'-10 1/8" | 12K3 | 10K1
 | 13'-0" | 5'-4" | 16KCS3 | 10K1
 | 11'-4" | 4'-9" | 16KCS3 | 10K1
 | 10'-0" | 4-9" | 12K5 | 10K1
 | 43'-8" | 5'-6 1/2" | 28K12 | 30K9
 | 10'-8" | 6'-2" | 12K3 | 10K1
 | 25'-8" | 5'-7 1/2" | 20K6 | 24K4
Section 5 | 13'-0" | 5'-10 3/4" | 12K3 | 10K1
 | 34'-4" | 5'-9" | 24K9 | 22K4
Joist Comparison

## Slide 32
North Pocono High School
Dan Hanley
Mechanical Option
Structural Breadth
Cost Comparison
Chart: Current System New System
Current System | 205461.9914 | 169542.0134
Material and Construction Cost
New System saves 17% of the Initial Cost

## Slide 33
North Pocono High School
Dan Hanley
Mechanical Option
Presentation Outline
Project Outline
Existing Mechanical System
Design Conditions
Air Side System
Hydronic System
ASHRAE Standards
Standard 90.1
Standard 62.1
Mechanical System Redesign
Redesign Objectives
Sizing the Ground Loop
Ground Source Heat Pump
Dedicated Outdoor Air System
System Comparison
Energy Comparison
Cost Comparison
Environmental Comparison
Structural Breadth
Load Comparison
Member Comparison
Cost Comparison
Electrical Breadth

## Slide 34
North Pocono High School
Dan Hanley
Mechanical Option
Electrical Breadth
Equipment | Amps | KVA
AHU-1 | 230.56 | 110.67
AHU-2 | 226.25 | 108.60
AHU-3 | 66.51 | 138.56
AHU-5 | 134.40 | 64.53
AHU-6 | 71.00 | 34.08
AHU-7 | 180.10 | 86.46
AHU-8 | 166.25 | 79.80
AHU-9 | 230.00 | 110.40
AHU-10 | 135.94 | 65.25
AHU-11 | 17.19 | 8.25
AHU-12 | 49.6 | 23.82
AHU-13 | 135.69 | 282.69
AHU-14 | 109.12 | 52.38
AHU-15 | 103.02 | 214.63
AHU-16 | 17.19 | 8.25
Pump-1 | 46.75 | 22.44
Pump-2 | 46.75 | 22.44
Pump-3 | 46.75 | 22.44
Boiler -1 | 6.33 | 13.19
Boiler -2 | 6.33 | 13.19
CU-2a | 230 | 110.4
CU-2b | 230 | 110.4
CU-3 | 75.81 | 157.93
CU-4 | 43.38 | 20.82
CU-5 | 43.38 | 20.82
Total | 2648.3 | 1902.44
Electrical Load Comparison
Equipment | Amps | KVA
DOAS-1 | 95.62 | 45.90
DOAS-2 | 105.63 | 50.70
DOAS-3 | 103.75 | 49.80
DOAS-5 | 67.50 | 32.40
DOAS-6 | 72.50 | 34.80
DOAS-7 | 88.12 | 42.30
DOAS-8 | 80.00 | 38.40
DOAS-9 | 175.00 | 84.00
DOAS-10 | 59.37 | 28.50
DOAS-11 | 49.37 | 23.70
DOAS-12 | 62.50 | 30.00
DOAS-13 | 292.50 | 140.40
DOAS-14 | 59.37 | 28.50
DOAS-15 | 80 | 38.4
Pump-1 | 46.75 | 22.44
Pump-2 | 46.75 | 22.44
RTG-1a | 67.36 | 32.34
RTG-1b | 67.36 | 32.34
RTG-1c | 67.36 | 32.34
RTG-2a | 40.31 | 19.35
RTG-2b | 40.31 | 19.35
Total | 1767.43 | 848.4
Current Electrical Data
New Electrical Data
33% Reduction in Amps
55% Reduction in KVA

## Slide 35
North Pocono High School
Dan Hanley
Mechanical Option
Electrical Breadth
Current Main Panel
Redesigned Main Panel

## Slide 36
North Pocono High School
Dan Hanley
Mechanical Option
Conclusions
$46 Million Increase in Mechanical First Cost
$187.4 Thousand in Utility Savings
Yearly Energy Consumption Reduced by 75%
Building Emissions Reduced by 75%
17% Material and Construction Cost for Smaller Roof Structure
Electrical Consumption was Reduced by 55%

## Slide 37
North Pocono High School
Dan Hanley
Mechanical Option
Acknowledgments
North Pocono School District
Crabtree Rohrbaugh Assoc.
Greenman and Pedersen Inc.
Penn State AE Faculty

## Slide 38
Thank You
Questions?