## Slide 1
The Mirenda Center for Sport Spirituality and Character Development
Zachary Heilman
Mechanical Option | 2011
Dr. Jim Freihaut | Dustin Eplee

## Slide 2
The Mirenda Center for Sport Spirituality and Character Development
$96,000
38 kBtu/ sf yr
$61,000
18 kBtu/ sf yr
$35,000
20 kBtu/ sf yr
Existing
Proposed
Savings

## Slide 3
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Cost Analysis
Mezzanine Proposal
Conclusion
Pennsylvania
U.S.A.
Aston
The Mirenda Center
Life & Learning Centers
Bachmann
The Circle
Neumann University

## Slide 4
Welcoming Center
Running Track & Main Gymnasium
Fitness Center

## Slide 5
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
6 Packaged Roof Top Units
Direct Expansion Cooling
Natural Gas Heating

## Slide 6
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Roof Top Unit (1)
Cost Analysis
Fitness Center
Classroom
Storage

## Slide 7
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Roof Top Unit (2)
Offices
Locker Room
Maintenance

## Slide 8
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Roof Top Unit (3 & 4)
Auxiliary
Gymnasium

## Slide 9
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Roof Top Unit (5 & 6)
Main Gymnasium
Running Track

## Slide 10
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Trane Trace Energy Model
  Internal Loads - people, lighting
  Ventilation Loads - 20% minimum
  Tmy Weather Data - Philadelphia
  Building Materials - walls, roof, slab
  Schedule of Use - wkday, wkend, summer, winter
Trace Input:
Chart: Modeled Building Load

## Slide 11
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
  * note CBECS is Commercial Buildings Energy Consumption Survey
COP=2.8
Cooling= 22 kBtu/ sf yr
Direct Expansion Cooling
0.85
Heating= 16 kBtu/ sf yr
Natural Gas Heating
Chart: DX- Cooling & Gas Heating to CBECS
| Existing | CBECS
 | 16 | 25
 | 22 | 15

## Slide 12
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Monthly Energy Cost - Existing
  N. Gas =$0.05/ ccf (1000 btu/ c.f.
  Consumption =$0.06 / kwh
  Demand (Dmd) =$6.21 / kw
  Ratchet = Dmd* 12 MONTHS
  $ Heating = $13,731
  $ Cooling = $82,735
  $ Totals = $96,466
Cost Analysis
Building Statistics

## Slide 13
Chart: 
| kWh | kW | RTCH
Ratchet | 36165.7652 | 46569.5195
kW | 16463.7725
kWh | 36165.7652
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Utility Rate Structure - Existing
  N. Gas =$0.05/ ccf (1000 btu/ c.f.
  Consumption =$0.06 / kwh
  Demand (Dmd) =$6.21 / kw
  Ratchet = Dmd* 12 MONTHS
  $ Heating = $13,731
  $ Cooling = $82,735
  $ Totals = $96,466
Cost Analysis
Building Statistics
  Cost Breakdown of Electricity

## Slide 14
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Ground Coupled Heat Pump
Cost Analysis

## Slide 15
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
  Well Sizing = 150 ft/ ton
  Cooling = 460 tons
  Heating = 1291 Mbh
  Depth of Well = 400 ft
  Wells Cooling = 172 wells
Ground Coupled HP System
Rule of Thumb
Cost Analysis
Chart: Modeled Building Load

## Slide 16
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
  Well Size = 171 ft/ton
  Cooling = 460 tons
  Heating = 1291 Mbh
  Depth of Well = 400 ft
  Wells Cooling = 199 wells
  Wells Heating = 42 wells
ASHRAE Calculation
Cost Analysis
Chart: Modeled Building Load
Ground Coupled HP System

## Slide 17
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
COP = 4.5
Heating = 4 kBtu/ sf yr
Cooling = 14 kBtu/ sf yr
20-40 ft ceiling height
Heat Pump Calculation
Chart: GCHP to CBECS
| GCHP | CBECS
 | 4 | 1.6
 | 16 | 13.6
Total Energy Comparison

## Slide 18
Chart: Monthly Energy Cost - GCHP
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
$ Cooling GCHP | 2399.8236 | 2588.5866 | 2584.6623 | 3073.4084 | 3729.2214 | 5280.5754 | 6775.9468 | 11251.5074 | 5182.4178 | 3183.162 | 2504.8201 | 2472.035
$ Heating GCHP | 1119.9152 | 1114.5348 | 479.6609 | 247.7533 | 140.8062 | 70.026 | 51.6815 | 95.0682 | 87.1958 | 179.8347 | 382.4932 | 599.2209
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
  Building Statistics
  $ Heating = $4,274
  $ Cooling = $51,026
  $ Total = $55,298
  Savings = $41,168
  Conventional DX Gas = $1.33/s.f.
  GCHP = $0.76/s.f.
Ground Coupled HP System

## Slide 19
Cost of (6) RTU | $476,269 | 
Unit Well Cost (Grout + Pipe + Drilling ) | $8,104 | $1,612,767
Distribution Piping Zone (2) Pipes per Zone | $1,990 | $33,007
Pumps + Elbows + Tees + Valves per zone | $650 | $10,779
Number of Wells | 199 | 
Number of Zones | 12 | 
Total Cost |  | $2,132,822
Cost of GCHP Wells |  | $1,656,553
Payback the Cost of Wells |  | 40
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Cost Analysis

## Slide 20
Cost of (6) RTU | $476,269 | 
Unit Well Cost (Grout + Pipe + Drilling ) | $8,104 | $1,612,767
Distribution Piping Zone (2) Pipes per Zone | $1,990 | $33,007
Pumps + Elbows + Tees + Valves per zone | $650 | $10,779
Number of Wells | 199 | 
Number of Zones | 12 | 
Total Cost |  | $2,132,822
Cost of GCHP Wells |  | $1,656,553
Payback the Cost of Wells |  | 40
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Cost Analysis

## Slide 21
Chart: % of 8760 hours
Chart: % of 8760 hours
Hybrid GCHP with Cooling Tower
Chart: % of 8760 hours

## Slide 22
Chart: Duration of Building Load
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Hybrid GCHP with Cooling Tower

## Slide 23
  Well Size = 171 ft/ton
  Cooling = 200 tons
  Heating = 1291 Mbh
  Depth of Well = 400 ft
  Wells Cooling = 70 wells
  Wells Heating = 42 wells
  Footprint = 27,976 ft2
  Pattern = 20 by 20 Grid
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
ASHRAE Calculation
Cost Analysis
Hybrid GCHP with Cooling Tower
Cost of (6) RTU | $476,269 | 
Well Cost (Grout + Pipe + Drilling ) | $8,104 | $567,305
Distribution Piping Zone (2) Pipes per Zone | $1,990 | $13,933
Pumps + Elbows + Tees + Valves per zone | $650 | $4,550
Cooling Tower |  | $50,000
Number of Wells | 70 | 
Number of Zones | 10 | 
Total Cost |  | $1,112,057
Cost of GCHP Wells |  | $635,788
Payback |  | 18

## Slide 24
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Cost Analysis
Cost Analysis
Chart: DX-Cooling & Gas Heating to GCHP
| Existing | GCHP | Savings
Existing | 16 | 4
CBECS | 22 | 14 | 16
  Energy Statistics
  Ex. Heating = 16 kBtu/ sf year
  Ex. Cooling = 22 kBtu/ sf year
  Ex. Total = 38 kBtu/ sf year
  GCHP Heating = 4 kBtu/ sf year
  GCHP Cooling = 14 kBtu/ sf year
  GCHP Total = 18 kBtu/ sf year
  Savings =20 kBtu/ sf year

## Slide 25
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Structural & Lighting Breadth
Cost Analysis
Mezzanine Proposal
Load & Resistance Factor Design – Conditions |  | 
Dead Load= | 40 | psf
Self-Weight= | 45 | psf
Live Load= | 80 | psf
Total Factored Load= | 1.2*(Dead)+1.6*(Live) | 
Mezzanine Width= | 12 | ft
Mezzanine Length= | 70 | ft
Total Thickness= | 5.5 | inches
Number of Bays= | 8 | 
Total Unfactored Load (no concrete self-weight)= | 120 | psf
Total Unfactored Load (with concrete self-weight)= | 165 | psf
Total Factored Load= | 230 | psf

## Slide 26
Introduction
Building Function
Existing Mechanical System
Ground Coupled Heat Pump
Mezzanine Proposal
Conclusion
Structural Breadth
Cost Analysis
Mezzanine Proposal
Load & Resistance Factor Design – Conditions |  | 
Dead Load= | 40 | psf
Self-Weight= | 45 | psf
Live Load= | 80 | psf
Total Factored Load= | 1.2*(Dead)+1.6*(Live) | 
Mezzanine Width= | 12 | ft
Mezzanine Length= | 70 | ft
Total Thickness= | 5.5 | inches
Number of Bays= | 8 | 
Total Unfactored Load (no concrete self-weight)= | 120 | psf
Total Unfactored Load (with concrete self-weight)= | 165 | psf
Total Factored Load= | 230 | psf

## Slide 27
Overview & Recommendation
Chart: DX-Cooling & Gas Heating to GCHP
| Existing | GCHP | Savings
Existing | 16 | 4
CBECS | 22 | 14 | 16
  Ex. Heating = 16 kBtu/ sf year
  Ex. Cooling = 22 kBtu/ sf year
  Ex. Total = 38 kBtu/ sf year
  GCHP Heating = 4 kBtu/ sf year
  GCHP Cooling = 14 kBtu/ sf year
  GCHP Total = 18 kBtu/ sf year
  Savings = 20 kBtu/ sf year
Cost of (6) RTU | $476,269 | 
Well Cost (Grout + Pipe + Drilling ) | $8,104 | $567,305
Distribution Piping Zone (2) Pipes per Zone | $1,990 | $13,933
Pumps + Elbows + Tees + Valves per zone | $650 | $4,550
Cooling Tower |  | $50,000
Number of Wells | 70 | 
Number of Zones | 10 | 
Total Cost |  | $1,112,057
Cost of GCHP Wells |  | $635,788
Payback |  | 18
  $ Savings = $35,321
  Conventional DX Gas = $1.33/s.f.
  GCHP = $0.84/s.f.
  Energy Statistics

## Slide 28
The Mirenda Center for Sport Spirituality and Character Development
Zachary Heilman
Mechanical Option | 2011
Dr. Jim Freihaut | Dustin Eplee
Thank you…