## Slide 1: Wentz Concert Hall and Fine Arts Center
http://www.educationdesignshowcase.com/view.esiml?pid=272
Will Lesieutre
Lighting / Electrical Option
Advisors: Dr. Mistrick, Prof. Dannerth

## Slide 2: Project Introduction
North Central College 171 E Chicago Ave Naperville, Illinois
Size: 57,000 ft2
Completed in 2008
605 seats
Second performing arts facility
Built for outstanding acoustics
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 3: Project Introduction
Aerial image via Bing Maps
"One of the most 'live' rooms in the area, its acoustics proved vivid and vibrant at all volume levels...Better still, the Wentz offered a clarity of orchestral detail lost in many other concert halls -Howard Reich, Chicago Tribune
Campus/Downtown location
Naperville’s first art gallery
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 4: Project Introduction
Owner: North Central College
Architect: Loebl Schlossman and Hackl
Lighting: Schuler Shook
Acoustics: Talaske
Construction: Gilbane
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Aerial image via Bing Maps

## Slide 5: Lighting Redesign Concepts
Design with linear architecture
Energy efficiency
Community landmark
Welcoming environment
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Image Credit: http://raoulpop.com/2010/02/09/cfl-vs-led-rate-of-adoption/

## Slide 6: Lighting Redesign Spaces
Main Lobby (Red)
Concert Hall (Blue)
Façade
Rehearsal Room (Green)
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 7: Main Lobby
Two stories high
Lower ceiling by main entry
  Coat check
  Box office
  Art gallery
Large curtain wall
  Interior visible from outside
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 8: Design Considerations
Illuminance
  15 fc horizontal at floor
    Avg:Min 3:1
  7.5 fc vertical at 5 ft. AFF
    Avg:Min 3:1
Dimmable to < 5 fc
Avoid glare
Reduce energy use
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 9: Solution
Primarily compact fluorescent
General illumination from downlights
Wall washers lighting wood wall
Linear LED arch to mark transition to concert hall
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 10: Performance
Average illuminance
  14.6 fc horizontal
    Target 15 fc
  5.0 fc vertical
    Target 7.5 fc
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Magenta: 10 fc Red: 15 fc

## Slide 11: [MAE] Flux Transfer Theory
Main lobby rendered using Radiance
Daylight is December 21st, 2 PM local time
Shows significant daylight penetration
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 12: Concert Hall
First floor and balcony level seating
Entrances at rear of first floor and sides of balcony
Levels separated by angular shelf
Control booth at rear below balcony
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 13: Design Considerations
Illuminance
  10 fc horizontal at floor
    Avg:Min 2:1
  3 fc vertical at 5 ft. AFF
    Avg:Min 2:1
Smooth dimming to 0%
Consistent color rendering
Noise sensitive space
Upper lighting positions restricted by catwalks
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 14: Solution
General illumination by incandescent downlights
Architectural accents using linear LEDs
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 15: Architectural Breadth
Create more opportunities for lighting
Enhance transition from seating to stage
Added a middle level shelf
  Produces an arched form on the side walls of the stage
  Integrates with linear lighting in other shelves
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 16: Performance
Average illuminance
  11.2 fc horizontal
    Target 10 fc
  2 fc vertical
    Target 3 fc
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Blue: 5 fc Magenta: 10 fc Red: 15 fc

## Slide 17: Facade
Large curtain walls
  Entries not in solid walls
Architectural precast panels
Metal cornice
High concert hall block
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
http://www.educationdesignshowcase.com/view.esiml?pid=272

## Slide 18: Design Considerations
Illuminance
  7.5 fc maximum to highlight façade features
  3 fc for large illuminated areas
Create a landmark appearance
  Should be recognizable from a distance at night
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
http://www.educationdesignshowcase.com/view.esiml?pid=272

## Slide 19: Solution
Light upper wall with color changing LEDs
Colored lighting uncommon in the area
  Makes the building highly visible
Allows lobby interior lighting to maintain high contrast
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 20: Rehearsal Room
Multifunction space
  Music classroom
  Rehearsal space
Two floors divided by technical shelf
No fixed furniture
  Seats and music stands are freely positionable
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 21: Design Considerations
Illuminance
  30 fc horizontal at floor
    Avg:Min 2:1
  20 fc vertical at 4 ft. AFF
    Avg:Min 2:1
  High vertical illuminance is required for reading sheet music
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 22: Solution
CFL downlights from ceiling
CFL uplights and asymmetric side lights from shelf
Linear fluorescent wall washers
Average illuminance
  28.8 fc horizontal
    Target 30fc
  20.1 fc vertical
    Target 20 fc
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Blue: 10 fc Magenta: 20 fc Red: 30 fc

## Slide 23: Transformer Consolidation
As designed, there are five transformers to serve 208/120V loads
Would it be more economical to use a single transformer?
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
www.everpowerelectric.com

## Slide 24: Transformers
One isolation transformer
Four eligible for replacement
Sized based on new central panelboard
  500 kVA
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Original Design |  | 
Tag | Transformer Size | Cost
1-TLDP-1 | 225 kVA | $8,624
1-TLDP-2 | 225 kVA | $8,624
LL-ELP-1 | 30 kVA | $2,800
LL-LDP-1 | 300 kVA | $10,690.00
Total |  | $30,738.00
Proposed Centralized Design |  | 
Tag | Transformer Size | Cost
TLL-LDP | 500 kVA | $16,325

## Slide 25: Panelboards
Original design requires one panel at the 120V side of each transformer
Redesign to feed a single panel
  Would still require some branch panels, this is an upper limit on savings
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Original Design |  | 
Tag | Panel Size | Cost
1-TLDP-1 | 800 A | $ 4,375.00
1-TLDP-2 | 1400 A | $ 5,625.00
LL-ELP-1 | 400 A | $ 2,860.00
LL-LDP-1 | 1200 A | $ 5,275.00
Total |  | $ 18,135.00
Proposed Centralized Design |  | 
Tag | Panel Size | Cost
LL-LDP | 4000 A | $ 12,200.00

## Slide 26: Feeders
Original 480/277V system can use smaller feeders
Wire size for 208/120V must be increased
  Higher material cost
  Higher labor cost
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Original Design |  |  |  |  |  |  |  | 
Load | Type | Phase/N | Ground | Raceway | Length (ft) | Feeder cost / ft | Raceway cost / ft | Total cost
T1-TLDP-1 | THHN | (3) 350 | 3 | 2 1/2" | 135 | 16.705 | 28.5 | $ 6,102.68
T1-TLDP-2 | THHN | (3) 350 | 3 | 2 1/2" | 165 | 15.03 | 28.5 | $ 7,182.45
LL-ELP-2 | THHN | (3) 8 | 10 | 3/4" | 15 | 4.28 | 10.25 | $ 217.95
LL-LDP-1 | THHN | (3) 500 | 3 | 3" | 30 | 20.72 | 36.2 | $ 1,707.60
FPC-ATS | THHN | (4) 1 | n/a | 1 1/4" | 25 | 8.48 | 14.85 | $ 583.25
LL-HDP-1 | THHN | 2x (4) 500 | 1/0 | 3 1/2" | 15 | 50.8 | 44.9 | $ 1,435.50
T1-DCTP-1 | THHN | (3) 1 | 8 | 1 1/4" | 155 | 7.515 | 14.85 | $ 3,466.58
Total: |  |  |  |  |  |  |  | $ 20,696.00
Proposed Centralized Design |  |  |  |  |  |  |  |  |  | 
Load | Design KVA | Design A | Type | Phase/N | Ground | Raceway | Length (ft) | Feeder cost / ft | Raceway cost / ft | Total cost
1-TLDP-1 | 133 | 369 | THHN | (4) 400 | 3 | 3" | 135 | 24.235 | 36.2 | $ 8,158.73
1-TLDP-2 | 146 | 405 | THHN | (4) 500 | 2 | 3" | 165 | 27.075 | 36.2 | $ 10,440.38
LL-ELP-1 | 30 | 83 | THHN | (4) 5 | 8 | 1" | 15 | 9.7 | 12.21 | $ 328.65
LL-LDP-1 | 244 | 677 | THHN | 2x (4) 350 | 2x 3 | 3 1/2" | 30 | 43.43 | 44.9 | $ 2,649.90
FPC-ATS | 80 | 222 | THHN | (4) 3/0 | 4 | 2" | 25 | 14.13 | 20.15 | $ 857.00
LL-LDP | 462 | 1282 | THHN | 3x (4) 500 | 3 | (3) 2 1/2" | 15 | 81.225 | 85.5 | $ 2,500.88
T1-DCTP-1 | 75 | 90 | THHN | (3) 1 | 8 | 1 1/4" | 165 | 7.515 | 14.85 | $ 3,690.23
Total: |  |  |  |  |  |  |  |  |  | $ 28,625.75

## Slide 27: Overall Cost
Centralized system is cheaper, disregarding branch panelboards
  If branch panelboards are unmodified, it will be more expensive
Single point of failure
  Can’t perform maintenance on part of system
Voltage drop
  Long connections at lower voltage may require larger feeders or branch circuits
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Category | Original Cost | Centralized Cost
Panels | $ 18,135.00 | $ 12,200.00
Transformers | $ 30,738.00 | $ 16,325.00
Feeders | $ 20,696.00 | $ 28,625.75
Total | $ 69,569.00 | $ 57,150.75

## Slide 28: Conclusions
More efficient lighting system
Accents architectural features
  Modified concert hall to support lighting
Creates a recognizable landmark
Centralized transformer may provide cost savings
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion

## Slide 29: Acknowledgements
Thesis Advisors
  Richard Mistrick
  Ted Dannerth
Other Faculty
  Kevin Houser
  Moses Ling
  Kevin Parfitt
  Bob Holland
Schuler Shook
  Jim Baney
  Emily Klingensmith
  Giulio Pedota
Friends and family
  Including all of you L/E students
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Questions?

## Slide 30
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Appendix A: Lighting Fixtures

## Slide 31: Main Lobby
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Type | Description | Manufacturer | Catalog Number | Lamp(s) | Input Watts
F1 | Unlensed 42W compact fluorescent downlight with 6" nominal aperture, white trim, and wheat reflector | Kurt Versen | P927DM-120-W-WT | (1) F42TBX/827/A/ECO by GE | 43.2
F2 | Unlensed 26W compact fluorescent downlight with 6" nominal aperture, white trim, and wheat reflector | Kurt Versen | P626DM-120-W-WT | (1) F26DBX/827/ECO4P by GE | 26.4
F3 | Unlensed 42W compact fluorescent wall washer with 6" nominal aperture, white trim, and wheat reflector | Kurt Versen | P953DM-120-W-WT | (1) F42TBX/827/A/ECO by GE | 43.2
F4 | Unlensed 18W compact fluorescent wall washer with 4" nominal aperture, white trim, and wheat reflector | Kurt Versen | P919DM-120-W-WT | (1) F18TBX/827/A/ECO by GE | 21.3
F5 | Shielded 3' T5 wall sconce with diffuse white acrylic panel | Lightolier | 48022ALU-21W-120 | (1) F21W/T5/830/ECO by GE | 25
F6 | Continuous diffuse LED strip light with dimmable driver | Birchwood Lighting | JAKE-325-TR-1-HF2N-H-30-CRx-120-CU | 54 3000K LEDs per 10" section | 5 W/ft

## Slide 32: Concert Hall
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Type | Description | Manufacturer | Catalog Number | Lamp(s) | Input Watts
F6 | Continuous diffuse LED strip light with dimmable driver | Birchwood Lighting | JAKE-325-TR-1-HF2N-H-30-CRx-120-CU | 54 3000K LEDs per 10" section | 5 W/ft
F7 | Top relampable 250W PAR38 halogen downlight with white trim | Kurt Versen | C7302-W-WT | 250PAR38HALFL30 by Sylvania | 250
F8 | Top relampable 90W PAR38 halogen downlight with white trim | Kurt Versen | C7302-W-WT | 90PAR/FL25XL-EG by GE | 90
F9 | Top relampable 75W PAR30 halogen downlight with white trim | Kurt Versen | C7301-W-WT | 75PAR30/H/FL35 by GE | 75
F10 | Linear LED neon-replacement with diffuse white light guide and dimmable driver | GE | GEWWXNLE1-30K-A | 3000K LEDs | 3.39 W/ft
F11 | LED steplight with black front-plate, fully shielded aperture, and dimmable driver | Cole Lighting | L-2158-BLK | 6W 3000K integrated LED | 8

## Slide 33: Facade
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Type | Description | Manufacturer | Catalog Number | Lamp(s) | Input Watts
F12 | Color changing linear LED fixture with 30x60 degree beam distribution in 2' nominal lengths. IP66 rated for outdoor use | Color Kinetics | 123-000030-03 | RGB LEDs | 35
F2 | Unlensed 26W compact fluorescent downlight with 6" nominal aperture, white trim, and wheat reflector | Kurt Versen | P626DM-120-W-WT | (1) F26DBX/827/ECO4P by GE | 26.4
F13 | Wall mounted LED grazer with 10° up and down beams | Beta-Calco | 66-2201 | (2) 3800K white LEDs | 4.5
F14 | Wet rated cylindrical up/downlight, wall mounted with convex lens | Delray Lighting | 242-BM-CUV8242.1E-WL | (2) F42TBX/830/A/ECO by GE | 43.2

## Slide 34: Rehearsal Room
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Type | Description | Manufacturer | Catalog Number | Lamp(s) | Input Watts
F15 | Recessed linear T5 fixture in 4' lengths with low iridescent louver | Peerless Lighting | LAR9-28T5-LDL-U4-120-C200 | (1) F28W/T5/830/ECO by GE | 26.8
F16 | Adjustable asymmetric CFL wall washer with lockable angle and semi gloss white finish | Winona Lighting | LS8-CFM142-120-P1-SGW-X-STD | (1) F42TBX/830/A/ECO by GE | 43.2
F17 | Semi-recessed asymmetric CFL with semi gloss white finish | Winona Lighting | LSRU-LR-CFM142-120-P1-SGW-X-STD | (1) F42TBX/830/A/ECO by GE | 43.2
F18 | Unlensed 42W compact fluorescent downlight with 6" nominal aperture, white trim, and wheat reflector | Kurt Versen | P927-120-W-WT | (1) F42TBX/830/A/ECO by GE | 43.2

## Slide 35
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Appendix B: Power Density

## Slide 36: Main Lobby
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Area: 7,167 ft2
Power Allowance: 2.0 W/ft2
Total lighting power (kW) 5.40 kW
Space power allowance (kW) 14.334 kW
Total decorative power 0.365 kW
Space decorative allowance 7.167 kW
Type | Quantity | Watts/Fixture | Type Total | Notes
F1 | 83 | 43.2 | 3585.6 W | 
F2 | 40 | 26.4 | 1056 W | 
F3 | 2 | 43.2 | 86.4 W | 
F4 | 29 | 21.3 | 617.7 W | 
F5 | 2 | 25 | 50 W | 
F6 | 73 ft | 5 W/ft | 365 W | Decorative

## Slide 37: Concert Hall
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Area: 5,921 ft2
Power Allowance: 2.43 W/ft2
Total lighting power (kW) 6.106 kW
Space power allowance (kW) 14.388 kW
Total decorative power 4.219 kW
Space decorative allowance 5.921 kW
Type | Quantity | Watts/Fixture | Type Total | Notes
F6 | 14 | 250 | 3500 W | 
F7 | 7 | 90 | 630 W | 
F8 | 24 | 75 | 1800 W | 
F9 | 654 ft | 5 W/ft | 3270 W | Decorative
F10 | 280 ft | 3.39 W/ft | 949.2 W | Decorative
F11 | 22 | 8 | 176 W | 

## Slide 38: Facade
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Illuminated Length 403 ft
Power Allowance 3.75 W/ft
Total lighting power (kW) 1.295 kW
Façade power allowance (kW) 1.511 kW
Type | Quantity | Watts/Fixture | Type Total | Notes
F12 | 37 | 35 | 1.295 W | 

## Slide 39: Rehearsal Room
Introduction
Design Concept
Lighting Designs
  Main Lobby
  Concert Hall
  Facade
  Rehearsal Room
Electrical Depth
Conclusion
Area: 2,045 ft2
Power Allowance: 1.24 W/ft2
Total lighting power (kW) 1.784 kW
Space power allowance (kW) 2.530 kW
Total decorative power 0.432 kW
Space decorative allowance 2.041 kW
Type | Quantity | Watts/Fixture | Type Total | Notes
F15 | 15 | 26.8 | 402 W | 
F16 | 10 | 43.2 | 432 W | Decorative
F17 | 12 | 43.2 | 518.4 W | 
F18 | 20 | 43.2 | 864 W |