## Slide 1
Northfield Mental Healthcare Center
Northfield, Ohio
Senior Thesis 2013
Ji Won Park
Mechanical Option
Advisor: Dr. Stephen Treado

## Slide 2
Function: mental clinic
SIZE: ~260,000 SF
(Additional 200,000 SF to existing 60,000 SF)
Overall Cost: ~62.5 million
Delivery Method: design-bid-build (multiple prime)
Construction Date: approx. April, 2013 – January, 2014
Northfield Mental Healthcare Center
Site Map
Building Information
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions

## Slide 3
Owner: Ohio Department of Mental Health
Architects: Hasenstab Architects, Inc.
Landscape: Bedell-Tucci, LLC (N/A)
MEP and Fire Protection: Scheeser Buckley Mayfield, LLC
Structural Engineers: Thorson Baker & Associates
Northfield Mental Healthcare Center
Project Overview
Project Team
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Provided high quality for care and safety
Designed to respect surrounding facilities
Provided additional recreation areas and therapeutic spaces
Used face brick exterior walls to match the existing building
Used smooth CMU, texted CMU, and curtain walls to highlight the new design

## Slide 4
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)
Air Side

## Slide 5
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 6
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 7
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 8
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 9
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 10
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Air Side
Existing:
Existing Constant Volume AHU (70,000 CFM)
Existing Constant Volume AHU (14,000 CFM)
Patient Wing Left / Right:
2 Custom AHUs (65,000 CFM Each) w/ DDC-VAV terminals
Clinc / Admin:
Variable Air Volume AHU (7,950 CFM) w/ DDC-VAV terminals
Dietary:
Variable Air Volume AHU (8,400 CFM) w/ DDC-VAV terminals
Gym:
Constant Volume AHU (3,700 CFM) w/ Sensible Wheel
Boiler Plant & Chiller Plant & Electrical Room
2 Constant Volume AHUs (5,000 CFM Each)
Variable Air Volume AHU (6,000 CFM)

## Slide 11
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Water Side
6 Natural Gas Fired Boilers (4,000 MBH each)
2 Electric Centrifugal Chillers (450 Tons each)
A 2-cell-cooling tower (Max. 900 Tons)

## Slide 12
Northfield Mental Healthcare Center
Existing Mechanical System
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Energy Efficient Devices
DDC-VAV terminals for AHU 1, 2, 4 & 5
VFD for supply and return fans for AHU 1, 2, 3, 4, 5 & 8
VFD for Secondary Heating Water Pumps
VFD for Secondary Chilled Water Pumps
VFD for Cooling Tower
VFD for Cooling Tower Pumps
Control System

## Slide 13
Northfield Mental Healthcare Center
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Load Summary
Existing Water Flow Diagram
Summary of Load | 
Cooling (TONS) | 834 TONS
Space Heating (MBH) | 11,180 MBH
Summary of Water Supply Needs | 
Chilled Water @11F Difference | 1,820 GPM
Hot Water @ 40F Difference | 560 GPM
Domestic Hot Water | 140 GPM

## Slide 14
Northfield Mental Healthcare Center
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Annual Energy Consumption Summary
Existing Water Flow Diagram
Summary of Annual Energy Consumption | 
Total Electricity Consumption | 14,127,906 KWh
Total Natural Gas Consumption | 636,589 Therms
Total Energy Consumption | 32,779,801 KWh
EUI Value Calculated | 
Electricity EUI | 185 kBtu / SF
Natural Gas EUI | 250 kBtu / SF
EUI | 435 kBtu / SF
EUI Value of Typical Hospital (Baseline Model) | 
EUI | 388 kBtu / SF

## Slide 15
Northfield Mental Healthcare Center
• Introduction
  • Northfield Mental Healthcare
  • Mechanical System
  • Design Goals
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Design Goals
Existing Water Flow Diagram
  Primary Goal:
  Reduce energy consumption
  Secondary Goal:
  Reduce emissions
EUI Value Calculated | 
Electricity EUI | 185 kBtu / SF
Natural Gas EUI | 250 kBtu / SF
EUI | 435 kBtu / SF
EUI Value of Typical Hospital (Baseline Model) | 
EUI | 388 kBtu / SF

## Slide 16
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
CHP System
Northfield Mental Healthcare Center
Combined Heat and Power (CHP) system
CHP supplies energy in two forms:
•Electricity
•Heat
Spark Spread
  Spark Spread
    Difference between electricity and gas rate in $/MMBtu
    Spark Spread >$12/MMBtu  CHP has the potential for favorable payback
Spark Spread | 
Determine the Average Annual Electric Cost ($/MMBtu) | 29.30
Determine the Average Gas Cost ($/MMBtu) | 7.550
Spark Spread | 22

## Slide 17
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Prime Mover Selection
T/P Ratio | 
1. Determine Thermal Use | 
Total Thermal Energy Delivered/Used | 63,658,920,000 Btu
2. Determine Electrical Use | 
Total Electric | 48,218,544,000 Btu
3. Determine T/P Ratio | 
T/P Ratio - Divide Total Thermal (Btu) by Total Electric (Btu): | 1.32
Recommended Prime Mover Technology Based on T/P Ratio | 
If T/P = | 
0.5 to 1.5 | Consider engines
1 to10 | Consider gas turbines
3 to 20 | Consider steam turbines
Prime Mover Selection
 | Capacity | Installation Costs | O&M Costs
Reciprocating Engines | 5 kWe - 20 MWe | $1,000 to $1,800 per kW | $0.010 to $0.015 per kWh
Gas Turbines | 25 kWe – 500 kWe | $800 to $1,500 per kW | $0.005 to $0.008 per kWh
Microturbines | 500 kWe – 100 kWe | $1,000 to $2,000 per kW | $0.010 to $0.015 per kWh

## Slide 18
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Primary Design |  | 
Building Size (SF) | Heating Baseline (MBH) | Heating Load (MBH)
260,000 | 5,640 | 11,180
Heating Baseline = Total Heating Load X 50% |  | 
CHP Module Sizing
CHP Module Selection
CHP COGENERATION MODULE - 2G 1540 NG | 
Reciprocating engine MWM® TCG2020 | 
Configuration | Natural Gas
Electrical Output | 1540 KW
Thermal Output | 1778 KW
Electrical Efficiency | 42.00%
Thermal Efficiency | 44.06%
Total efficiency | 80.06%
Thermal Heat | 6,066,787 Btu/h (Usable)
Water Flow rate High Temp | 17,100 Gph
Water Temp | 194F
Fuel Consumption | 12508 MBtu/h
Energy Consumption | 8,122 Btu / kW

## Slide 19
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Primary Design |  | 
Building Size (SF) | Heating Baseline (MBH) | Heating Load (MBH)
260,000 | 5,640 | 11,180
Heating Baseline = Total Heating Load X 50% |  | 
CHP Module Selection
CHP COGENERATION MODULE - 2G 1540 NG | 
Reciprocating engine MWM® TCG2020 | 
Configuration | Natural Gas
Electrical Output | 1540 KW
Thermal Output | 1778 KW
Electrical Efficiency | 42.00%
Thermal Efficiency | 44.06%
Total efficiency | 80.06%
Thermal Heat | 6,066,787 Btu/h (Usable)
Water Flow rate High Temp | 17,100 Gph
Water Temp | 194F
Fuel Consumption | 12508 MBtu/h
Energy Consumption | 8,122 Btu / kW
CHP Module Sizing

## Slide 20
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
CHP Module Internal Structure
CHP Module Selection
CHP COGENERATION MODULE - 2G 1540 NG | 
Reciprocating engine MWM® TCG2020 | 
Configuration | Natural Gas
Electrical Output | 1540 KW
Thermal Output | 1778 KW
Electrical Efficiency | 42.00%
Thermal Efficiency | 44.06%
Total efficiency | 80.06%
Thermal Heat | 6,066,787 Btu/h (Usable)
Water Flow rate High Temp | 17,100 Gph
Water Temp | 194F
Fuel Consumption | 12508 MBtu/h
Energy Consumption | 8,122 Btu / kW

## Slide 21
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
CHP Module Simple Payback Period
Northfield Mental Healthcare Center
Heat Recovery | 
Heat Recovery | 6,068,314 Btu/hr
Heating Load | 11,180,000 Btu/hr
Heat Recovery Basis Efficiency | 60%
Energy Generation & Fuel Consumption | 
Annual Electric Generation | 13,490,400 kWh
Annual Thermal Generation | 53,158 MMBtu
Annual Fuel Consumption | 109,570 MMBtu
Revenue | 
Electric Revenue | $1,349,040
Thermal Revenue | $401,346
Total Revenue | $1,750,386
Expenses | 
Fuel Expenses | $827,254
O&M Costs | $168,630
Standby Charge | $55,440
Total Expenses | $1,051,324
Saving | 
Total Saving | $699,062

## Slide 22
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
CHP Module Simple Payback Period
Northfield Mental Healthcare Center
Heat Recovery | 
Heat Recovery | 6,068,314 Btu/hr
Heating Load | 11,180,000 Btu/hr
Heat Recovery Basis Efficiency | 60%
Energy Generation & Fuel Consumption | 
Annual Electric Generation | 13,490,400 kWh
Annual Thermal Generation | 53,158 MMBtu
Annual Fuel Consumption | 109,570 MMBtu
Revenue | 
Electric Revenue | $1,349,040
Thermal Revenue | $401,346
Total Revenue | $1,750,386
Expenses | 
Fuel Expenses | $827,254
O&M Costs | $168,630
Standby Charge | $55,440
Total Expenses | $1,051,324
Saving | 
Total Saving | $699,062

## Slide 23
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
CHP Module Simple Payback Period
Northfield Mental Healthcare Center
Revenue | 
Electric Revenue | $1,349,040
Thermal Revenue | $401,346
Total Revenue | $1,750,386
Expenses | 
Fuel Expenses | $827,254
O&M Costs | $168,630
Standby Charge | $55,440
Total Expenses | $1,051,324
Saving | 
Total Saving | $699,062
Payback | 
First Cost | $2,310,000
Total Saving | $699,062
Simple Payback | 3.30 Yrs

## Slide 24
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Cogeneration Schematic
Northfield Mental Healthcare Center
Cogeneration Schematic

## Slide 25
• Introduction
• Alternative 1: Cogeneration
  • CHP System
  • CHP Module Simple Payback
  • Cogeneration Schematic
  • Cogeneration Energy Saving
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Annual Energy Consumption
Northfield Mental Healthcare Center
Annual Net Saving
 |  | Annual Energy Generated |  | Annual Energy Consumption (Space Heating &Space Cooling) | 
 |  | Thermal (MMBtu) | Electricitiy (KWh) | Thermal (MMBtu) | Electricitiy (KWh)
Existing | Heating | - | - | 103,091 | -
 | Cooling |  |  | - | 4,204,800
Alternative 1 | Heating | 53,138 | 13,490,400 | 78,840 | -
 | Cooling |  |  | - | 4,204,800
 | Annual Net Saving |  |  |  | 
 | Thermal (MMBtu) | Electricitiy (KWh) | Thermal ($) | Electricitiy ($) | Total ($)
Existing vs. Alternative1 | 24,251 | 13,490,400 | 183,098 | 1,349,040 | 1,532,138

## Slide 26
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
  • CHPC System
  • Tri-generation Schematic
  • Tri-generation Energy Saving
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
CHPC System
Absorption Chiller Selection
Combined Heat, Power and Cooling (CHPC) system
CHPC supplies energy in three forms:
•Electricity
•Heat
•Chilled water
Absorption Chiller Selection | 
Carrier 16JLR 47 | 
(Single Effect Lithium Bromide - Water Absorption Chiller) | 
Cooling Capacity | 450 Tons
Chilled Water Temp | 54 / 44 F
Cooling Water Temp | 85 / 95 F
Hot Water Temp | 203 / 185 F
COP | 0.7
Chiller Type | Heat Production (Brtu/kWh) |  | Absorber COP |  | Cooling Available (Tons/kW) | 
 | Min. | Max. | Min. | Max. | Min. | Max.
Single Effect | 3,800 | 6,000 | 0.70 | 0.78 | 0.22 | 0.35
Double Effect | 1,500 | 2,000 | 1.10 | 1.30 | 0.15 | 0.20

## Slide 27
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
  • CHPC System
  • Tri-generation Schematic
  • Tri-generation Energy Saving
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
CHPC System
Absorption Chiller Selection
Combined Heat, Power and Cooling (CHPC) system
CHPC supplies energy in three forms:
•Electricity
•Heat
•Chilled water
Absorption Chiller Selection | 
Carrier 16JLR 47 | 
(Single Effect Lithium Bromide - Water Absorption Chiller) | 
Cooling Capacity | 450 Tons
Chilled Water Temp | 54 / 44 F
Cooling Water Temp | 85 / 95 F
Hot Water Temp | 203 / 185 F
COP | 0.7
Chiller Type | Heat Production (Brtu/kWh) |  | Absorber COP |  | Cooling Available (Tons/kW) | 
 | Min. | Max. | Min. | Max. | Min. | Max.
Single Effect | 3,800 | 6,000 | 0.70 | 0.78 | 0.22 | 0.35
Double Effect | 1,500 | 2,000 | 1.10 | 1.30 | 0.15 | 0.20

## Slide 28
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
  • CHPC System
  • Tri-generation Schematic
  • Tri-generation Energy Saving
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Tri-generation Schematic
Heating Side Schematic

## Slide 29
Northfield Mental Healthcare Center
Tri-generation Schematic
Cooling Side Schematic
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
  • CHPC System
  • Tri-generation Schematic
  • Tri-generation Energy Saving
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions

## Slide 30
Northfield Mental Healthcare Center
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
  • CHPC System
  • Tri-generation Schematic
  • Tri-generation Energy Saving
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Annual Energy Consumption
Annual Net Saving
 |  | Annual Energy Generated |  | Annual Energy Consumption (Space Heating &Space Cooling) | 
 |  | Thermal (MMBtu) | Electricitiy (KWh) | Thermal (MMBtu) | Electricitiy (KWh)
Existing | Heating | - | - | 103,091.37 | -
 | Cooling |  |  | - | 4,204,800
Alternative 2 | Heating | 53,138 | 13,490,400 | 80,296.93 | -
 | Cooling |  |  |  | 2,890,800
 | Annual Net Saving |  |  |  | 
 | Thermal (MMBtu) | Electricitiy (KWh) | Thermal ($) | Electricitiy ($) | Total ($)
Existing vs. Alternative2 | 22,794 | 14,804,400 | 172,098 | 1,480,440 | 1,652,538

## Slide 31
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
  • Annual Energy Cost
  • Emission
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Comparison- Annual Net Saving
Northfield Mental Healthcare Center
 | Annual Net Saving |  |  |  | 
 | Thermal (MMBtu) | Electricitiy (KWh) | Thermal ($) | Electricitiy ($) | Total ($)
Existing vs. Alternative1 | 24,251 | 13,490,400 | 183,098 | 1,349,040 | 1,532,138
Existing vs. Alternative2 | 22,794 | 14,804,400 | 172,098 | 1,480,440 | 1,652,538
Alternative2 vs. Alternative 1 | (1,457) | 1,314,000 | (11,000) | 131,400 | 120,400
  Alternative 1: More Saving on First Cost
  Alternative 2: More Saving on Annual Energy Consumption
First Cost | Existing | Alternative 1 | Alternative 2
Boilers | $2,280,000 | $1,387,000 | $1,900,000
Electric Chiller | $304,000 | $304,000 | $152,000
Absorption Chiller | $0 | $0 | $180,000
Pumps | $400,000 | $400,000 | $400,000
Total | $2,984,000 | $2,091,000 | $2,632,000
Saving On First Cost | $0 | $893,000 | $352,000
Comparison- First Cost

## Slide 32
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
  • Annual Energy Cost
  • Emission
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Emission- Alternative 1
Annual Emissions Analysis - Alternative 1 |  | 
 | Emissions/Fuel Reduction | Percent Reduction
NOx (tons/year) | (4.452) | (0.469)
SO2 (tons/year) | 22.205 | 0.998
CO2 (tons/year) | 4,369 | 0.362
CH4 (tons/year) | 0.090 | 0.384
N2O (tons/year) | 0.122 | 0.894
Total GHGs (CO2e tons/year) | 4,408 | 0.364
Carbon (metric tons/year) | 1,080 | 0.362
Fuel Consumption (MMBtu/year) | 22,298 | 0.145
Number of Cars Removed | 765 | 
Annual Emissions Analysis - Alternative 2 |  | 
 | Emissions/Fuel Reduction | Percent Reduction
NOx (tons/year) | 1.317 | 0.086
SO2 (tons/year) | 40.830 | 0.999
CO2 (tons/year) | 9,350 | 0.548
CH4 (tons/year) | 0.191 | 0.568
N2O (tons/year) | 0.227 | 0.940
Total GHGs (CO2e tons/year) | 9,425 | 0.550
Carbon (metric tons/year) | 2,312 | 0.548
Fuel Consumption (MMBtu/year) | 63,561 | 0.326
Number of Cars Removed | 1,637 | 
Emission- Alternative 2

## Slide 33
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
  • Code Analysis
  • Load Distribution Analysis
  • Sizing Conductors
• Summary
• Acknowledgements
• Questions
Electrical Breadth
Northfield Mental Healthcare Center
Code Analysis
NEC 517.31 and NFPA 99 3-4.3.1
Emergency generator Startup time (Healthcare facility) < 10 s
CHP system cannot serve for the life safety load & critical load.
Replacing existing emergency generator with CHP generator

## Slide 34
Northfield Mental Healthcare Center
Emergency Generator - Existing
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
  • Code Analysis
  • Load Distribution Analysis
  • Sizing Conductors
• Summary
• Acknowledgements
• Questions
Load Distribution - Existing

## Slide 35
Northfield Mental Healthcare Center
Load Distribution Analysis
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
  • Code Analysis
  • Load Distribution Analysis
  • Sizing Conductors
• Summary
• Acknowledgements
• Questions
Load Distribution - Existing
 | Percentage (%)
Critical & Life Safety | 50.2
Equipment System | 49.8
Total | 100
Each of existing emergency generators serves 50% of total emergency load.
Gen #1 is big enough to serve as the life safety load and critical load.
Gen #2 will be replaced by the CHP generator.

## Slide 36
Northfield Mental Healthcare Center
Load Distribution Analysis
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
  • Code Analysis
  • Load Distribution Analysis
  • Sizing Conductors
• Summary
• Acknowledgements
• Questions
Load Distribution – New Design
 | Percentage (%)
Critical & Life Safety | 50.2
Equipment System | 49.8
Total | 100
Each of existing emergency generators serves 50% of total emergency load.
Gen #1 is big enough to serve as the life safety load and critical load.
Gen #2 will be replaced by the CHP generator.

## Slide 37
Northfield Mental Healthcare Center
Conductors Sizing
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
  • Code Analysis
  • Load Distribution Analysis
  • Sizing Conductors
• Summary
• Acknowledgements
• Questions
Load Distribution – New Design
NEC 445.13. Over Current Protection For Generator : 115%
Sizing Conductors |  | 
Electrical Output | 1,540 | KW
Power Factor | 0.90 | 
Voltage | 480 | V
Amps | 1,667 | A
Over Current Protection (115%) | 1,917 | A
Up sized: 4 set of # 750 MCM, 1 set of #750 G MCM |  | 

## Slide 38
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Net Saving
Northfield Mental Healthcare Center
Emission
 | Alternative 1 | Alternative 2
 | Percent Reduction | 
Carbon (metric tons/year) | 36% | 55%
Fuel Consumption (MMBtu/year) | 14% | 33%
 | Alternative 1 | Alternative 2
Net Saving ($) | 1,532,138 | 1,652,538
  Primary Goal:
  Reduce energy consumption
  Secondary Goal:
  Cut back on emissions

## Slide 39
• Introduction
• Alternative 1: Cogeneration
• Alternative 2: Tri-generation
• Comparison
• Breadth: Electrical Breadth
• Summary
• Acknowledgements
• Questions
Northfield Mental Healthcare Center
Northfield Mental Healthcare Center
Special Thanks to:
James D. Freihaut, PhD – Professor of AE Dept.
Moses D. F. Ling, PE, RA – Associate Professor of AE Dept.
Stephen Treado, Ph.D., P.E. –Associate Professor of AE Dept.
William P. Bahnfleth, PhD, PE - Professor, AE Dept.
Doug Smelker– Scheeser Buckley Mayfield LLC
Jason Wilson – Scheeser Buckley Mayfield LLC
Josh Roehm – Scheeser Buckley Mayfield LLC
Questions?