## Slide 1
Hershey Research Park Building One
Jonathan Krepps
Structural Option
Senior Thesis 2013
Faculty Advisor: Dr. Hanagan

## Slide 2
Presentation Outline
Building Introduction
Existing Conditions
Structural Depth – Structural Redesign
Breadth One – Sustainability
Breadth Two – Mechanical
Conclusion
Comments

## Slide 3
Building Introduction
Hershey, PA
Research Facility
80,000 square feet
Three Stories, 50 feet tall
Construction started in April 2006
Opened in May 2007
$10.7 Million
Project Team
Owner: Wexford Technology, LLC
Architect: Ayers/Saint/Gross Inc.
Engineers: Brinjac Engineering
Construction Mangers: Whiting – Turner Construction
Site Master Plan

## Slide 4
Existing Structural System
Steel Moment Frame
Composite Metal Deck
  Vulcraft 3VLI18
Piers with Concrete Caps
Deck Cross Section
Typical Floor Frame

## Slide 5
Existing Structural System
Steel Moment Frame
Composite Metal Deck
  Vulcraft 3VLI18
Piers with Concrete Caps
Deck Cross Section
Lateral Frame

## Slide 6
Lateral Frame
RAM Model - Lateral Frame
RAM Model – Existing Structure

## Slide 7
Structural Depth
System Redesign
  Steel to Concrete
  One Way Slab with Beams
Lateral Design
  Concrete Moment Frame
Goals
  Design an adequate system
  Cost effective and easy to construct
Thesis Breadths
Breadth One – Sustainability
Breadth Two – Mechanical
Goals
  LEED Certification through the addition of green roof
  More energy efficient

## Slide 8
Redesign Details
Controlling Load Combination
  1.2D + 1.6L
Live Load = 100 psf
Superimposed Dead Load = 25 psf
Total Load = 190 psf
Table 9.5(a) of ACI used to help determine beam depths
As = Mu / 4d
Slab Design
Span Length
  10.67 ft
Slab Thickness
  5.5 in
Slab Weight
  68.75 psf
Reinforcement
  Flexural - # 4 bars @ 12 in OC
  Transverse - # 4 bars @ 18 in OC
32.5’
B1
B2
G1
32’
Typical Bay

## Slide 9
Redesign Details
Controlling Load Combination
  1.2D + 1.6L
Live Load = 100 psf
Superimposed Dead Load = 25 psf
Total Load = 190 psf
Table 9.5(a) of ACI used to help determine beam depths
As = Mu / 4d
Beam B1 Design
Span Length
  32.5 ft
Beam Section
  16” x 28”
Mu = 237 k-ft < ΦMn = 264 k-ft
Vu = 39 k < ΦVn = 78 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (4) # 7 bars
  # 4 Stirrups
32.5’
B1
B2
G1
32’
Typical Bay

## Slide 10
Beam B2 Design
Beam B1 Design
Span Length
  32.5 ft
Beam Section
  16” x 28”
Mu = 237 k-ft < ΦMn = 264 k-ft
Vu = 39 k < ΦVn = 78 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (4) # 7 bars
  # 4 Stirrups
32.5’
B1
B2
G1
32’
Span Length
  32.5 ft
Beam Section
  20” x 28”
Mu = 247 k-ft < ΦMn = 267 k-ft
Vu = 41 k < ΦVn = 88 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (4) # 7 bars
  # 4 Stirrups
Typical Bay

## Slide 11
Beam B2 Design
Girder Design
Span Length
  32 ft
Beam Section
  20” x 28”
Mu = 302 k-ft < ΦMn = 333 k-ft
Vu = 47 k < ΦVn = 117 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (5) # 7 bars
  # 4 Stirrups
32.5’
B1
B2
G1
32’
Span Length
  32.5 ft
Beam Section
  20” x 28”
Mu = 247 k-ft < ΦMn = 267 k-ft
Vu = 41 k < ΦVn = 88 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (4) # 7 bars
  # 4 Stirrups
Typical Bay

## Slide 12
Column Design
Girder Design
Span Length
  32 ft
Beam Section
  20” x 28”
Mu = 302 k-ft < ΦMn = 333 k-ft
Vu = 47 k < ΦVn = 117 k
Reinforcement
  Exterior Spans – (3) # 7 bars
  Interior Spans – (5) # 7 bars
  # 4 Stirrups
32.5’
B1
B2
G1
32’
Column Layout Unchanged
Simplified Design for Columns
  Alsamsam and Kamara
Design Aids based of ACI
Column Section
  20” x 20”
Reinforcement
  (12) # 10 bars
Max Load
  Pu = 564 kips < ΦPn = 1050 kips
Typical Bay

## Slide 13
Lateral Redesign
Concrete Moment Frame
No addition lateral resisting needed
Analysis done using RAM Structural System
Controlling Load Cases
  Wind – 1.2 D + 1.0 L + 1.0 W
  Seismic – 1.2 D + 1.0 L + 1.0 E
RAM Structural Model
RAM Structural Model

## Slide 14
Wind Loads
ASCE 7 – 10
Load Combination
  1.2 D + 1.0 L + 1.0 W
  Wind Case One
Max Story Drift
  H/400
RAM Structural Model
Serviceability
Controlling Wind Load Case 1.2D+1.0L+1.0W |  |  |  |  | 
Floor | X Deflection (in) | Y Deflection (in) | X Drift (in) | Y Drift (in) | Allowable Drift (in)
Roof | 0.059 | 0.02152 | 0.0124 | 0.01 | 0.44
3rd | 0.04666 | -0.01148 | 0.0231 | 0.0066 | 0.44
2nd | 0.0236 | -0.00485 | 0.0236 | 0.0049 | 0.44
Total |  |  | 0.0591 | 0.0215 | 

## Slide 15
Seismic Loads
ASCE 7 – 10
Load Combination
  1.2 D + 1.0 L + 1.0 E
Max Story Drift
  0.015 x H
Design Variables
  Seismic Design Category = “D”
  R = 3.0
  I = 1.25
RAM Structural Model
Serviceability
Controlling Seismic Load Case 1.2D+1.0L+1.0E |  |  |  |  | 
Floor | X Deflection (in) | Y Deflection (in) | X Drift (in) | Y Drift (in) | Allowable Drift (in)
Roof | 0.51621 | -0.019 | 0.1492 | 0.0008 | 2.64
3rd | 0.36698 | -0.00981 | 0.2005 | 0.0059 | 2.64
2nd | 0.16647 | -0.00424 | 0.1664 | 0.0045 | 2.64
Total |  |  | 0.5161 | 0.0112 | 

## Slide 16
Sustainability Breadth
Main goal is to achieve LEED certification through the addition of a green roof
Owners Future Plans – LEED Certification for all buildings
Two different green roofs were compared
  LiveRoof
  TectaGreen
Roof Structure
  Extra 35 psf on Roof

## Slide 17
Sustainability Breadth
Both designs have similar advantages and disadvantages
The LiveRoof system was chosen as the better choice
Standard Module
Possible of obtaining over 20 LEED credits
Optimized Energy Performance – Mechanical Breadth
LiveRoof System |  | 
LEED Category | Credit Abbreviation | Credits Possible
Protect or Restore Habitat and Maximum Open Space | SS 5.1/5.2 | 1 each (2 total)
Storm Water Design | SS 6.1/6.2 | 1 each (2 total)
Heat Island Effect | SS 7.1/7.2 | 1 each (2 total)
Water Efficient Landscape | WE 1.1/1.2 | 2/4 (6 total)
Optimized Energy Performance | EA 1.1-1.19 | 1 each (19 total)
Construction Waste Management | MR 2 | 1 to 2
Recycled Content | MR 4.1/4.2 | 1 to 2
Regional Materials | MR 5.1/5.2 | 1 to 2
Rapidly Renewable Materials | MR 6 | 1
LiveRoof Green Roof Design Detail

## Slide 18
Sustainability Breadth
Both designs have similar advantages and disadvantages
The LiveRoof system was chosen as the better choice
Standard Module
Possible of obtaining over 20 LEED credits
Optimized Energy Performance – Mechanical Breadth
LiveRoof Green Roof Design Detail
LiveRoof Green Roof

## Slide 19
Structural Effects
Roof Loads
  Roof Live Load – 30 psf
  Superimposed Dead Load – 25 psf
  Green Roof – 35 psf
  Snow Load – 30 psf
Controlling Load Case
  1.2 D + 1.6 Lr
Total Load – 120 psf
LiveRoof Green Roof
Roof Slab Design Details | 
Slab Thickness | 5.5”
Flexural Reinforcement (Top and Bottom) | # 4 Bars @ 12”
Transverse Reinforcement | # 4 Bars @ 18”
System Weight | 68.75 psf
Roof Beam Design Details | 
Beam Section | 12”x22”
Flexural Reinforcement (Exterior Spans) | (3) #7 Bars
Flexural Reinforcement (Interior Spans) | (2) #10 Bars
Beam Weight | 206 plf
Roof Girder Design Details | 
Beam Section | 18”x22”
Flexural Reinforcement (Midspan) | (3) #7 Bars
Flexural Reinforcement (Supports) | (5) #7 Bars
Beam Weight | 310 plf

## Slide 20
Breadth Conclusion
The addition of a green roof would be helpful
LEED credits can help for LEED certification
  Certified: 40 – 49 points
  Silver: 50 – 59 points
  Gold: 60 – 79 points
  Platinum: 80 or more
LiveRoof Green Roof

## Slide 21
Conclusions
The existing steel frame is the more feasible structural system for the building
  Higher floor thickness
  Longer construction time
The addition of a green roof would be helpful
  Possible addition of over 20 LEED Credits
  LEED Certification
  Lower energy cost

## Slide 22
Comments
Or
Questions?
Acknowledgements
Wexford Science and Technology, LLC
Brinjac Engineering
Ayers/Saint/Gross Inc.
AE Staff
Advisor: Dr. Linda Hanagan

## Slide 23
Mechanical Breadth
Main goal was to find the energy saving ability of the green roof
The more energy the green saves, the better
More LEED Credits
  Optimized Energy Performance – Mechanical Breadth
  Up to 19 Credits Possible

## Slide 24
Mechanical Breadth
Main goal was to find the energy saving ability of the green roof
The more energy the green saves, the better
More LEED Credits
  Optimized Energy Performance – Mechanical Breadth
  Up to 19 Credits Possible
Roof Assembly R - Values | 
Material | R – Value
Concrete Slab (5.5”) | .4125
Insulation | 22
Roof Board | 1.09
Water Proofing Membrane | .12
LiveRoof Standard Green Roof System | 2
Green Roof Assembly

## Slide 25
Mechanical Breadth
Energy Saving of 77,375,928 BTU per year
Additional financial benefits from tax credits
  Federal – 30% of total cost
LEED points
  One Credit from energy reduction
Roof Assembly R - Values | 
Material | R – Value
Concrete Slab (5.5”) | .4125
Insulation | 22
Roof Board | 1.09
Water Proofing Membrane | .12
LiveRoof Standard Green Roof System | 2
Green Roof Assembly