## Slide 1
Oklahoma University Children’s
Medical Office Building
Oklahoma City, O.K.
Alec Canter, BAE
Mechanical Option
Advisor: Laura Miller

## Slide 2
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
  VRF System
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
  VRF Indoor Units
  Design Criteria
  Room Noise Criteria
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Presentation Outline
N

## Slide 3
Project Background:
  Building Statistics
  Layout
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Project Background
Building Statistics
Location: Oklahoma City, Oklahoma
Size (Gross Square Feet): 337,000
12 Stories Above Grade, 1 Below
Function: Medical Office Building
Overall Project Cost: $ 60,000,000
Construction: Spring 2006 – Spring 2009
N

## Slide 4
Project Background:
  Building Statistics
  Layout
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Project Background
Floor Layout
N
Room Locations
Offices, patient Rooms, and conference rooms populate the North and East exterior faces.
Waiting areas and the main lobby are located on the South and West side
All other labs, exam rooms, and special equipment rooms such a X-ray rooms dominate the interior

## Slide 5
Project Background
Existing Conditions:
  Mechanical System
  Design Conditions
  Energy Model Evaluation
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Existing Conditions
Mechanical Design
Mechanical Room Locations
Floor-by-floor air handling systems
12 Air Handling Units in Total
Utilizes hydronic heat and cooling supplied by central plant to main mechanical room in the basement
VAV terminal units distribute air to each space
Heating water for zone reheat

## Slide 6
Project Background
Existing Conditions:
  Mechanical System
  Design Conditions
  Energy Model Evaluation
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Existing Conditions
Climate Zone
Design Conditions
Oklahoma City resides in Climate Zone 3A, which is characterized as being Warm-Humid
Design Settings | Summer | Winter
Outdoor Air Dry Bulb [oF] | 96 | 17
Outdoor Air Wet Bulb [oF] | 75 | -
Relative Humidity [%RH] | 50 | 
Indoor Air Dry Bulb [oF] | 75 | 72
Indoor Air Wet Bulb [oF] | 62 | 60

## Slide 7
Project Background
Existing Conditions:
  Mechanical System
  Design Conditions
  Energy Model Evaluation
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Existing Conditions
Air Handling Unit Schedule
Energy Summary
Chart: Annual Energy Consumption
| Heating | Cooling | Fans & Pumps | Lighting & Receptacle
 | 2796067 | 3351931 | 969706 | 5742841
Floor | Design vs. Calculated Airflow |  | 
 | Designed [cfm] | Calculated [cfm] | Percent Error
Basement | 15000 | 10929 | 27.14
Third | 25000 | 25854 | 3.42
Fourth | 25000 | 25498 | 1.99
Fifth | 25000 | 25829 | 3.32
Sixth | 25000 | 26242 | 4.97
Seventh | 25000 | 25692 | 2.77
Eighth | 25000 | 26070 | 4.28
Ninth | 25000 | 23254 | 6.98
Tenth | 25000 | 23039 | 7.84

## Slide 8
Project Background
Existing Conditions:
  Mechanical System
  Design Conditions
  Energy Model Evaluation
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Existing Conditions
Emissions
Energy Consumption
Chart: Pollutants
| SO2 | NOx
 | 33.9489 | 21.9712
Estimated CO2 Emissions: 6,152,946 lbm/year
Estimated Nox and SO2 Emissions: 56 lbm/year
Total CO2 Equivalent Emissions: 6,153,002 lbm/year
Energy Consumption | 
Site Energy [Btu/ft2-yr] | 86724
Source Energy [Btu/ft2-yr] | 234585
Chart: Total Energy Consumption [Btu/ft2-year]
| Site Energy [Btu/ft2-yr] | Source Energy [Btu/ft2-yr]
 | 86724 | 234585

## Slide 9
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Thesis Goals
Propose a system that could:
  Reduce energy use
  Reduce operating costs
  Reduce emissions
  Improve occupant temperature control
Energy Usage
Operating Costs
Emissions
Occupant Comfort

## Slide 10
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Plan
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Design a Variable Refrigerant Flow (VRF) system to serve each floor
  Condenser units will be located on the roof
  Indoor units will be paired with a DOAS
Replace existing air handling units on each floor to serve to zones 100% outdoor air and treat incoming air
  Indoor units will be ducted and served by DOAS

## Slide 11
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Basic VRF Design
VRF with Heat Recovery
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Cooling Mode
Basic Refrigeration Cycle
Heating Mode
Reverse Heat Pump Cycle
Outdoor Condensing Unit becomes Evaporator Unit

## Slide 12
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Loads per Floor
 | Exterior Peak Cooling [BTU/h] | Exterior Peak Cooling [Tons] | Equipment Cooling Capacity [Tons] | Interior Peak Cooling [BTU/h] | Interior Peak Cooling [Tons] | Equipment Cooling Capacity [Tons]
Floor 0 | - | - | - | 249004 | 20.75 | 20.00
Floor 3 | 355162 | 29.60 | 28.00 | 122452 | 10.20 | 10.00
Floor 4 | 311954 | 26.00 | 26.00 | 150737 | 12.56 | 12.00
Floor 5 | 327911 | 27.33 | 26.00 | 141228 | 11.77 | 12.00
Floor 6 | 364400 | 30.37 | 28.00 | 143120 | 11.93 | 12.00
Floor 7 | 363766 | 30.31 | 28.00 | 122886 | 10.24 | 10.00
Floor 8 | 353628 | 29.47 | 28.00 | 122504 | 10.21 | 10.00
Floor 9 | 310667 | 25.89 | 28.00 | 88743 | 7.40 | 12.00
Floor 10 | 335795 | 27.98 | 28.00 | 82749 | 6.90 | 8.00
Typical Floor Layout
N
Floor | Cooling [tons] | Heating [MBH]
0 | 20.8 | 106.9
3 | 40.4 | 59.5
4 | 39.0 | 60.4
5 | 39.6 | 56.2
6 | 42.9 | 61.3
7 | 41.1 | 60.7
8 | 40.3 | 61.1
9 | 33.8 | 51.5
10 | 35.4 | 53.4

## Slide 13
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Loads by Floor
Zone Design
Floor | Cooling [tons] | Heating [MBH]
0 | 20.8 | 106.9
3 | 40.4 | 59.5
4 | 39.0 | 60.4
5 | 39.6 | 56.2
6 | 42.9 | 61.3
7 | 41.1 | 60.7
8 | 40.3 | 61.1
9 | 33.8 | 51.5
10 | 35.4 | 53.4
Basement Floor Zone Designation

## Slide 14
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Typical Zone Layout
Zone Design
4th Floor
5th Floor
6th Floor
7th Floor
8th Floor
9th Floor
10th Floor
3rd Floor Zone Designation

## Slide 15
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Condenser Schedule
General Design Requirements
Floor/Units | Condenser Unit Sizes | 
 | Interior Zone [tons] | Exterior Zone [tons]
F0/CU-1,CU-2 | 20 | -
F3/CU-3,CU-4 | 10 | 28
F4/CU-5,CU-6 | 12 | 26
F5/CU-7,CU-8 | 12 | 26
F6/CU-9,CU-10 | 12 | 28
F7/CU-11,CU-12 | 10 | 28
F8/CU-13,CU-14 | 10 | 28
F9/CU-15,CU-16 | 8 | 26
F10/CU-16,CU-17 | 8 | 28
540 linear feet of piping between condensing unit and furthest located fan coil unit or equivalent
3,280 total one-way piping in the complete piping network
164 feet in vertical separation between the condensing unit and the fan coil units
49 feet in vertical separation between fan coil units

## Slide 16
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Evaluation
System Power Requirements
Chart: Monthly Electricity Consumption
| January | February | March | April | May | June | July | August | September | October | November | December
VRF-Redesign | 215484 | 195638 | 213241 | 215644 | 229837 | 233608 | 255314 | 245270 | 222210 | 215855 | 202440 | 215768
VAV-Existing | 240053 | 217692 | 245338 | 245291 | 257173 | 253381 | 264785 | 262631 | 248455 | 250138 | 238035 | 240055
Chart: Existing VAV Design
| January | February | March | April | May | June | July | August | September | October | November | December
Lights & Receptacles | 142909.02 | 129078.93 | 142909 | 138298.86 | 142908.92 | 138299.05 | 142908.84 | 142909 | 138298.86 | 142908.83 | 138298.95 | 142908.98
Cooling | 77297.32 | 70573.98 | 81836.95 | 86302.7 | 92910.15 | 94027.74 | 99683.43 | 97904.64 | 89689.28 | 86365.18 | 80019.45 | 77326.97
Heating | 115629.58 | 105114.22 | 118426.38 | 118480.89 | 123788.93 | 122420.17 | 128797.56 | 126919.6 | 118808.12 | 119271.76 | 113121.38 | 115456.71

## Slide 17
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Evaluation
System Power Requirements
Chart: Proposed VRF Redesign
| January | February | March | April | May | June | July | August | September | October | November | December
Lights & Receptacles | 142909.02 | 129078.93 | 142909 | 138298.86 | 142908.92 | 138299.05 | 142908.84 | 142909 | 138298.86 | 142908.83 | 138298.95 | 142908.98
Cooling | 47343.12 | 43271 | 48979.25 | 59439.9 | 67948.21 | 76153.61 | 91993.7 | 82537.36 | 65983.69 | 55480.93 | 46157.01 | 46245.8
Heating | 25232.04 | 23287.8 | 21353.05 | 17904.65 | 18980.02 | 19155.55 | 20411.71 | 19824.01 | 17927.54 | 17464.65 | 17983.63 | 26612.73
Chart: Monthly Electricity Consumption
| January | February | March | April | May | June | July | August | September | October | November | December
VRF-Redesign | 215484 | 195638 | 213241 | 215644 | 229837 | 233608 | 255314 | 245270 | 222210 | 215855 | 202440 | 215768
VAV-Existing | 240053 | 217692 | 245338 | 245291 | 257173 | 253381 | 264785 | 262631 | 248455 | 250138 | 238035 | 240055

## Slide 18
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Required Airflow Comparison
Fan Utilization
Floor | Required Airflow |  | 
 | Original Design [cfm] | Redesign [cfm] | Percent Difference
Basement | 10929 | 8912 | 18.46
Third | 25854 | 25225 | 2.43
Fourth | 25498 | 18438 | 27.69
Fifth | 25829 | 21691 | 16.02
Sixth | 26242 | 23180 | 11.67
Seventh | 25692 | 21704 | 15.52
Eighth | 26070 | 25412 | 2.52
Ninth | 23254 | 19379 | 16.66
Tenth | 23039 | 20708 | 10.12
Total | 212407 | 184648 | 13.07
Fan Energy Savings |  | 
Original Design [kBtu/yr] | Redesign [kBtu/yr] | Energy Saved [kBtu/yr]
969,700 | 741,400 | 228,300

## Slide 19
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth:
  VRF Design
  Dedicated Outdoor Air System
  Evaluation
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Mechanical Depth
Energy
Emissions
Energy Consumption Breakdown | Existing [kBtu/yr] | Redesign [kBtu/yr] | Reduction [kBtu/yr]
Heating | 2796067 | 98689 | 2697378
Cooling | 3351931 | 2496724 | 855207
Fans & Pumps | 969706 | 741378 | 228328
Lighting & Receptacle | 5742841 | 5742841 | -
Total | 12860545 | 9079632 | 3780913
Total Operating Cost:
Existing: $298,360/year, $1.55/ft2
Redesign: $179,028/year, $0.93/ft2
Total Annual Savings: $119,332
Existing CO2 Equivalent Production: 6,153,002 lbm/year
Redesign CO2 Equivalent Production: 3,951,153 lbm/year
Total Reduction: 2,201,849 lbm/year ~64% Decrease
Occupant Comfort
It is implied VRF Heat Recovery system design creates increased controllability by allowing simultaneous heating and cooling for occupant comfort

## Slide 20
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth:
  VRF Indoor Units
  Design Criteria
  Room Noise Criteria
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Acoustics Breadth
Sound Power Levels
Indoor Unit Types
Model FXMQ_PVJU Ducted Concealed |  |  | 
Cooling Capacity |  | Sound Levels (dBA) | 
BTU/h | Tons | Cooling | Heating
7500 | 0.6 | 29 | 33
9500 | 0.75 | 29 | 333
12000 | 1 | 29 | 34
18000 | 1.5 | 37 | 41
24000 | 2 | 38 | 42
30000 | 2.5 | 39 | 43
36000 | 3 | 39 | 43
48000 | 4 | 40 | 44

## Slide 21
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth:
  VRF Indoor Units
  Design Criteria
  Room Noise Criteria
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Acoustics Breadth
Existing Sound Power Levels
VRF with DOAS Units
Octave Band (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Supply Fan Power Level, Lw (dB) | 94 | 94 | 88 | 87 | 85 | 83 | 78 | 72
Return Power Level, Lw (dB) | 84 | 86 | 77 | 77 | 76 | 74 | 64 | 60
Combined Sound Power Level, Lw (dB) | 94 | 95 | 88 | 87 | 86 | 84 | 78 | 72
Octave Band (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Supply Fan Power Level, Lw (dB) | 90 | 91 | 85 | 84 | 84 | 81 | 76 | 71
Exhaust Fan Power Level, Lw (dB) | 76 | 77 | 76 | 73 | 71 | 68 | 65 | 60
Combined Sound Power Level, Lw (dB) | 90 | 91 | 86 | 84 | 84 | 81 | 76 | 71
Octave Band (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
VAV Sound Power Level, Lw (dB) | 60 | 60 | 54 | 44 | 42 | 39 | 34 | 34
Octave Band (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
VRF Sound Power Level, Lw (dB) | 44 | 49 | 40 | 37 | 38 | 34 | 22 | 14

## Slide 22
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth:
  VRF Indoor Units
  Design Criteria
  Room Noise Criteria
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Acoustics Breadth
Spectrum Noise Levels
Octave Band (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
VAV-AHU Sound Power Level at Room | 60 | 63 | 62 | 23 | 6 | 0 | 43 | 44
VAV-AHU Sound Pressure Level | 49 | 52 | 51 | 12 | 0 | 0 | 32 | 33
VRF-DOAS Sound Power Level at Room | 55 | 60 | 58 | 13 | 0 | 0 | 7 | 6
VRF-DOAS Sound Pressure Level | 44 | 49 | 47 | 2 | 0 | 0 | 0 | 0
Chart: Noise Criteria for Waiting Room 0300
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC-15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC-20 | 51 | 40 | 33 | 26 | 22 | 19 | 17 | 16
NC-25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC-30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC-35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC-40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
NC-45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC-50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC-55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC-60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC-65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
 | 83 | 79 | 75 | 73 | 71 | 69 | 68 | 67

## Slide 23
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth:
  VRF Indoor Units
  Design Criteria
  Room Noise Criteria
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Acoustics Breadth
NC-Ratings by Floor
Evaluation
NC-Rating |  |  | 
Floor | Room Designation | Existing | Redesign
0 | Waiting Room | 42 | 37
3 | Exam Room | 45 | 46
4 | Faculty Office | 45 | 38
5 | Exam Room | 44 | 45
6 | Vitals Area | 51 | 55
7 | Dictation Room | 53 | 54
8 | Consultation | 51 | 49
9 | Reception Area | 39 | 33
10 | Shared Break Room | 50 | 50
Noise Criteria levels are based on the background noise present within the space
Overall, 50% of the rooms investigated with the combine VRF-DOAS system performed better than the existing VAV spectrum levels
The rooms that performed worse were within the standard Noise Criterion levels
Additionally, those that performed worse were within 4 NC-values
Therefore, the design is sufficient without needing any redesign

## Slide 24
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Conclusion
Overall Evaluation
VRF System with DOAS Investigation:
Increased Occupant Control
Decreased Energy Consumption
Decreased Operating Costs
Decreased Emissions
Recommended
Indoor Unit Acoustic Investigation:
Remains consistent with existing design
50% of spaces studied had improved background noise level with the indoor units and DOAS
Meets standard NC rating room requirements

## Slide 25
Project Background
Existing Conditions
Thesis Goals
Mechanical Depth
Acoustics Breadth
Conclusion
Mechanical Option
Oklahoma University Children’s MOB
Alec Canter
Conclusion
Special Thanks:
The Pennsylvania State University Architectural Engineering Department
Thesis Advisor: Dr. Laura Miller
Jorge Charneco, AIA; Miles Associates
Thanks to all my family and friends

## Slide 26
Questions?