## Slide 1: The Medical Office Building
Kale Mullikin
Mechanical Option
Advisor: Donghyun Rim

## Slide 2: The Medical Office Building Overview
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Located in North-East United State
Exam, Physical Therapy, Radiology, Small Lab
~73,000 SF
$21.9 Million
Currently Under Construction
Exam
Physical Therapy
Radiology

## Slide 3: The Medical Office Building Existing Conditions
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Packaged Rooftop Units
  70 Ton
  VAV Reheat
Ductless Split System Units
Propane and Electric
 | Summer Design Cooling (0.4%) | Winter Design Heating (99.6%)
Outdoor Air Dry Bulb (°F) | 92.4 | 9.4
Outdoor Air Wet Bulb (°F) | 74.1 | -
Indoor Air Design Temp (°F) | 75 | 72

## Slide 4: The Medical Office Building Trane Modeling
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Trane TRACE 700
Blocks Defined As:
  Conference
  Corridor
  Lobby
  Office
  Physical Therapy
  Procedure
  Reception
  Storage
115 Tons
$46,060 Yearly Utility
 | Electric (kWh) | Gas (kBtu) | Total Building Energy (kBtu/yr)
Heating | - | 709,240 | 709,240
Cooling | 204,744 | - | 698,791
Lighting | 529,746 | - | 1,808,024
Receptacles | 115,781 | - | 395,161
 |  |  | 3,611,216

## Slide 5: The Medical Office Building Trane Modeling
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion

## Slide 6: The Medical Office Building Ground Coupled Motivation
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Large area for ground coupled placement
Eliminate need for propane gas
Potential for large energy savings
Reduce Emissions

## Slide 7: The Medical Office Building Vertical Well
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Required well length of 10,702 ft
  15% factor of safety
36 wells needed
  300’ well depth
Well Depth (ft) | Required Length | Number of Wells
100 | 10702 | 108
200 | 10702 | 54
300 | 10702 | 36

## Slide 8: The Medical Office Building Horizontal Well
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Required Length of 10,702ft
  15% factor of safety
13 - 800ft runs
1 – 400ft run
10,800ft total

## Slide 9: The Medical Office Building Cost Analysis – Rooftop Units
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Trane Axiom GER 300
  25 Ton Capacity
 | Original Units | New Units
Cost per Unit | $62,650 | $24,975
Number of Units | 2 | 5
Total Cost | $125,300 | $124,875

## Slide 10: The Medical Office Building Cost Analysis - Wells
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Utility cost after - $42,115
Savings - $3,945
 | Vertical Well | Horizontal Well
Cost per Unit Length | $10.57 | $1.12
Total Length | 10,702 | 10,800
Pipe & Fitting Cost | - | $6,048
Total Cost | $114,156 | $18,144
Simple Payback | 28.9 years | 4.6 years
Discounted Payback | - | 4.9 years

## Slide 11: The Medical Office Building Loads & Original Design
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
24K4 Roof Joist
W18X35 Mechanical Joist
Loads
  Snow Load – 20psf
  Live Load – 30psf
  Dead Load – 8psf
  Collateral – 7psf
  Mechanical Dead Load – 75psf

## Slide 12: The Medical Office Building Joist Redesign
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
42nd Edition Catalog of Standard Specifications and Load and Weight Tables for Steel Joists and Joist Girders
New Joists: 20LH08

## Slide 13: The Medical Office Building Girder Redesign
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Original Girders
  W24X55 Edge
  W24X68 Center
Redesign Girders
  W21X55 Edge
  W21X73 Center

## Slide 14: The Medical Office Building Cost Comparison
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Savings of $32,724
Original Design |  |  | 
Member | Cost per Member | # of Members | Total Cost
W18X35 | $1,530.00 | 28 | $42,840.00
W24X55 | $2,640.00 | 10 | $26,400.00
W24X68 | $2,970.00 | 2 | $5,940.00
 |  |  | $75,180.00
Redesign |  |  | 
Member | Cost per Member | # of Members | Total Cost
20LH08 | $522.00 | 28 | $14,616.00
W21X55 | $2,190.00 | 10 | $21,900.00
W21X73 | $2,970.00 | 2 | $5,940.00
 |  |  | $42,456.00

## Slide 15: The Medical Office Building Conclusion/Recommendations
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Ground coupled system
  Saves $3,945/year
  Vertical Well – Payback of 28.9 years
  Horizontal Well – Payback of 4.9 years
Roof framing redesign
  20LH08 Joists
  W21X55 and W21X73 Girders
  Save $32,724

## Slide 16: The Medical Office Building Acknowledgements
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Dr. Donghyun Rim – Advisor
Kurt Hutter - Anchor Health Properties
Randy Cook - The Procz Group Inc.
Family and Friends

## Slide 17: The Medical Office Building Appendices - Charts
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
 | Summer Design Cooling (0.4%) | Winter Design Heating (99.6%)
Outdoor Air Dry Bulb (°F) | 92.4 | 9.4
Outdoor Air Wet Bulb (°F) | 74.1 | -
Indoor Air Design Temp (°F) | 75 | 72
 | Electric (kWh) | Gas (kBtu) | Total Building Energy (kBtu/yr)
Heating | - | 709,240 | 709,240
Cooling | 204,744 | - | 698,791
Lighting | 529,746 | - | 1,808,024
Receptacles | 115,781 | - | 395,161
 |  |  | 3,611,216

## Slide 18: The Medical Office Building Appendices - Charts
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Well Depth (ft) | Required Length | Number of Wells
100 | 10702 | 108
200 | 10702 | 54
300 | 10702 | 36
 | Original Units | New Units
Cost per Unit | $62,650 | $24,975
Number of Units | 2 | 5
Total Cost | $125,300 | $124,875
 | Vertical Well | Horizontal Well
Cost per Unit Length | $10.57 | $1.12
Total Length | 10,702 | 10,800
Pipe & Fitting Cost | - | $6,048
Total Cost | $114,156 | $18,144
Simple Payback | 28.9 years | 4.6 years
Discounted Payback | - | 4.9 years

## Slide 19: The Medical Office Building Appendices - Charts
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion
Original Design |  |  | 
Member | Cost per Member | # of Members | Total Cost
W18X35 | $1,530.00 | 28 | $42,840.00
W24X55 | $2,640.00 | 10 | $26,400.00
W24X68 | $2,970.00 | 2 | $5,940.00
 |  |  | $75,180.00
Redesign |  |  | 
Member | Cost per Member | # of Members | Total Cost
20LH08 | $522.00 | 28 | $14,616.00
W21X55 | $2,190.00 | 10 | $21,900.00
W21X73 | $2,970.00 | 2 | $5,940.00
 |  |  | $42,456.00

## Slide 20: The Medical Office Building Appendices - Figures
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion

## Slide 21: The Medical Office Building Appendices - Figures
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion

## Slide 22: The Medical Office Building Appendices - Figures
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion

## Slide 23: The Medical Office Building Appendices - Figures
    Overview
    Existing Conditions
    Ground Coupled Depth
      System Design Options
      Cost Analysis
    Structural Breadth
      Joist Redesign
      Girder Redesign
      Cost
    Conclusion