## Slide 1: Ft. Detrick Defense Medical Logistics Center Building Systems Redesign

## Slide 2: Outline
  Background
  Existing Mechanical Systems
  Redesign Summary
  Redesign Goals
  Mechanical Depth Study
  Architectural/Site Breadth Study
  Electrical Breadth Study
  Conclusions and Recommendations

## Slide 3: Background
Size
129,960 ft2
Cost
$26.5 Million
Function
Office
Occupants
Top Medical Planning Organizations within the Department of Defense, representing the Army, Navy, Air Force, and Marines

## Slide 4: Background
AT/FP
Anti-Terrorism/Force Protection
SPiRiT
Sustainable Project Rating Tool

## Slide 5: Existing Mechanical System
Chilled Water System
2 Water-Cooled Chillers at 220 tons each
42°F Leaving Water Temperature
Serves Cooling Coils of AHU-1 thru 6
Hot Water System
2 Gas-Fired Boilers at 2160 MBH each
Serves AHU heating coils, VAV reheat coils, and Unit Heaters
Personal Photo Taken 2/23/08
Personal Photo Taken 2/23/08

## Slide 6: Existing Mechanical System
Airside
6 VAV Air Handling Units
Water Heating and Cooling Coils
VAV Hot Water Reheat Boxes
Personal Photo Taken 2/23/08

## Slide 7: Existing Mechanical System
First Floor
Second Floor
Third Floor

## Slide 8: Redesign Goals
Decrease Space
Increase Energy Efficiency
Maintain Affordability
Maintain Occupant Safety
Improve Sustainability

## Slide 9: Redesign Summary
Mechanical Depth Study
  DOAS/Chilled Beams/High-Induction Diffusers
Architectural/Site Breadth Study
  Constructed Wetland for On-Site Wastewater Treatment
Electrical Breadth Study
  Impact of Mechanical Redesign on Electrical System

## Slide 10: Dedicated Outdoor Air System (DOAS)
Enthalpy Wheel
  Recovers Energy
  Save on Utility Cost
Innovent Dedicated Outdoor Air Unit
Mechanical Depth Study

## Slide 11: Dedicated Outdoor Air System (DOAS)
100% Outdoor Air
  Smaller Volume of Air Required
  Contaminants Not Recirculated
Mechanical Depth Study
 | Vot (current design) | Vot 100% OA (∑Voz) | Difference
AHU-1 | 4460 | 2843 | 
AHU-3 | 4975 | 2235 | 
AHU-5 | 4670 | 2120 | 
Total | 14,105 | 7198 | 6907
 | Vot (current design) | Vot 100% OA (∑Voz) | Difference
AHU-2 | 4210 | 1773 | 
AHU-4 | 4550 | 2092 | 
AHU-6 | 4985 | 2584 | 
Total | 13,745 | 6449 | 7296
Outdoor Air Savings from DOAS-1
Outdoor Air Savings from DOAS-2

## Slide 12: Mechanical Depth Study

## Slide 13: Mechanical Depth Study
Chilled Beams
Passive System
  Cool by Convection and Radiation
  Remove Sensible Loads
  No Additional Energy to Operate
http://www.aeieng.com/services/sustainable/chilledbeam.htm

## Slide 14: Mechanical Depth Study
High-Induction Diffusers
Cooling Supply Air Temperature = 48°F
  Diffusers encourage mixing of air
  Prevent “dumping” of cold air
Nailor High-Induction Diffuser

## Slide 15: Mechanical Depth Study
Goal 1 – Decrease Space
Existing System
  6 Mechanical Rooms
  5.2% Lost Rentable Space
Redesigned System
  2 Mechanical Rooms
  3.3% Lost Rentable Space
Owner saves 2392 ft2 – 2% of Total Area

## Slide 16: Mechanical Depth Study
Goal 2 – Increase Energy Efficiency
Chart: Weekday Cooling Load - June
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Current Design | 46.7 | 40.3 | 35 | 29.9 | 28 | 28.3 | 29.7 | 77.8 | 153.8 | 196.1 | 206.2 | 201 | 174.5 | 203.3 | 240.8 | 233.7 | 239.6 | 189.1 | 151.8 | 125.6 | 102.4 | 68.8 | 61.7 | 54.6
DOAS/CB | 15.4 | 14.2 | 12.9 | 11.8 | 11.2 | 10.7 | 10.8 | 42.4 | 45.5 | 55.7 | 65.5 | 72.8 | 84.5 | 97.4 | 108 | 114.1 | 115.3 | 107.8 | 96.7 | 88.7 | 77.9 | 32.9 | 27.4 | 22.7

## Slide 17: Mechanical Depth Study
Goal 2 – Increase Energy Efficiency
Chart: Weekday Heating Load - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Current Design | 464.388 | 479.057 | 492.24 | 503.195 | 505.052 | 499.667 | 498.805 | 873.87 | 649.921 | 369.465 | 177.92 | 85.102 | 71.97 | 50.128 | 32.935 | 30.112 | 29.047 | 29.372 | 1.932 | 36.579 | 203.625 | 326.52 | 405.559 | 425.893
DOAS/CB | 7.312 | 15.454 | 31.448 | 65.062 | 73.574 | 95.846 | 117.326 | 651.685 | 502.558 | 339.376 | 259.273 | 177.912 | 132.106 | 93.864 | 63.03 | 49.086 | 47.349 | 75.718 | 88.932 | 103.634 | 127.29 | 0.014 | 0.014 | 3.648

## Slide 18: Mechanical Depth Study
Existing System Energy Cost: $164,529/year
Redesigned System Energy Cost: $136,252/year
Yearly Savings: $28,277
Goal 3 – Maintain Affordability
Utility Rates - Baltimore Gas and Electric |  |  | 
Utility Type | Rate Type | Summer Charge | Winter Charge
Electric Consumption | On Peak | $0.07/kWh | $0.055/kWh
Electric Consumption | Off Peak | $0.044/kWh | $0.04/kWh
Electric Demand | On Peak | $10.22/kW | $4.94/kW
Electric Demand | Off Peak | $4.94/kW | $4.94/kW
Gas Consumption | - | $0.4165/therm | 

## Slide 19: Mechanical Depth Study
Existing System First Cost: $296,000
Redesigned System First Cost: $384,050
First Cost Increase: $88,050
Goal 3 – Maintain Affordability
Initial Cost Comparison |  |  | 
Equipment | Existing System | Redesign DOAS/CB | Difference
Diffusers (493) | $20,460 | $21,300 | -$840
VAV Boxes (164) | $87,740 | $ - | $87,740
Chilled Beams (1460) | $ - | $276,750 | -$276,750
VAV AHUs (6) | $187,800 | $ - | $187,800
DOAS Units (2) | $ - | $86,000 | -$86,000
Total | $296,000 | $384,050 | -$88,050

## Slide 20: Mechanical Depth Study
Existing System Life Cycle Cost: $1,696,733
Redesigned System First Cost: $1,544,041
20-Year Life Cycle Cost Savings: $152,692
  Payback Period: only 3.9 years
Goal 3 – Maintain Affordability

## Slide 21: Mechanical Depth Study
Goal 4 – Maintain Occupant Safety
Simulation of contaminant released in outdoor air intake (star)
Concentration of contaminants 30 minutes following release
Existing system has higher initial concentration on first floor
  Smaller Zones
  Rest of contamination due to leakage
1st Floor 2nd Floor 3rd Floor
Existing System
Redesigned System

## Slide 22: Mechanical Depth Study
Goal 4 – Maintain Occupant Safety
Redesign takes approximately 2 hours longer to clear the building
Chart: Concentration vs. Time Classroom 129
| 0 | 2.0833333333333412E-2 | 4.1666666666666664E-2 | 6.25E-2 | 8.3333333333333343E-2 | 0.104166666666667 | 0.125 | 0.14583333333333395 | 0.16666666666666666 | 0.18750000000000044 | 0.20833333333333395 | 0.22916666666666666 | 0.25 | 0.27083333333333326 | 0.29166666666666796 | 0.312500000000001 | 0.33333333333333331 | 0.35416666666666796 | 0.375000000000001 | 0.39583333333333331 | 0.41666666666666796 | 0.437500000000001 | 0.45833333333333326 | 0.47916666666666796 | 0.5 | 0.5208333333333337 | 0.54166666666666652 | 0.5625 | 0.58333333333333337 | 0.60416666666666652 | 0.62500000000000211 | 0.64583333333333603 | 0.66666666666666663 | 0.6875 | 0.7083333333333337 | 0.72916666666666652 | 0.75000000000000211 | 0.77083333333333603 | 0.79166666666666652 | 0.8125 | 0.8333333333333337 | 0.85416666666666652 | 0.87500000000000211 | 0.8958333333333337 | 0.91666666666666652 | 0.9375 | 0.9583333333333337 | 0.97916666666666652 | 1
Existing | 0 | 280558.4493 | 152237.4536 | 68759.8167 | 29895.5725 | 12901.0893 | 5565.1758 | 2391.6458 | 1032.5471 | 446.1339 | 191.7916 | 82.5578 | 35.6447 | 15.3387 | 6.6 | 2.8516 | 1.2257 | 0.52892 | 0.22767 | 0.098195 | 0.042314 | 0.018213 | 0.0078418 | 0.0033805 | 0.0014557 | 0.00062781 | 0.00027136 | 0.00011659 | 5.0133e-05 | 2.1617e-05 | 9.3136e-06 | 4.0244e-06 | 1.7293e-06 | 7.4509e-07 | 3.2195e-07 | 1.3821e-07 | 5.9561e-08 | 2.5756e-08 | 1.1061e-08 | 4.7603e-09 | 2.0536e-09 | 8.8537e-10 | 3.8174e-10 | 1.642e-10 | 7.083e-11 | 3.0585e-11 | 1.3131e-11 | 5.6572e-12 | 2.4376e-12
Redesign | 0 | 157986.6022 | 122571.8471 | 80028.1478 | 50592.5072 | 31735.3 | 19938.0472 | 12510.1472 | 7841.8386 | 4921.2712 | 3081.5436 | 1929.4143 | 1209.6209 | 758.8876 | 476.0295 | 298.9557 | 186.9623 | 117.0527 | 73.3591 | 45.9932 | 28.7457 | 18.0753 | 11.3373 | 7.1059 | 4.4613 | 2.7826 | 1.75 | 1.0969 | 0.6876 | 0.43234 | 0.27136 | 0.16948 | 0.10624 | 0.06669 | 0.041624 | 0.026216 | 0.016397 | 0.010279 | 0.006439 | 0.0040474 | 0.0025296 | 0.0015868 | 0.00099575 | 0.00062321 | 0.00039094 | 0.00024606 | 0.00015362 | 9.6356e-05 | 6.0481e-05

## Slide 23: Mechanical Depth Study
Goal 4 – Maintain Occupant Safety
Acute Exposure Guideline Level (AEGL)
  Describe risk from one-time exposure to contaminants
Contaminant selected arbitrarily, only intended to display relative concentration between 2 cases
Redesign never reaches dangerous level – 2 hour difference is not critical
Chart: Concentration vs. Time - Classroom 129 Acute Exposure
| 0 | 1.1574074074074081E-4 | 2.0833333333333377E-2 | 4.1666666666666664E-2 | 6.25E-2 | 8.3333333333333343E-2 | 0.10416666666666677 | 0.125 | 0.14583333333333356 | 0.16666666666666666 | 0.18750000000000022 | 0.20833333333333356 | 0.22916666666666666 | 0.25 | 0.27083333333333326 | 0.29166666666666713 | 0.31250000000000039 | 0.33333333333333331
Existing | 0 | 0.005 | 0.011 | 0.015 | 0.006 | 0.0025 | 0.001 | 0.0005 | 0.00025 | 0.000125 | 6e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Redesign | 0 | 0.001 | 0.0025 | 0.00375 | 0.00225 | 0.00125 | 0.0008 | 0.0005 | 0.00025 | 0.0002 | 0.0001 | 5e-05 | 2.5e-05 | 1.25e-05 | 6e-06 | 0 | 0 | 0
AEGL 2 | 0.015 | 0.0085 | 0.006 | 0.005 | 0.0043 | 0.004 | 0.0036 | 0.0032 | 0.0029 | 0.0027 | 0.0025 | 0.0024 | 0.0023 | 0.00225 | 0.0022 | 0.0022 | 0.0022

## Slide 24: Mechanical Depth Study
Existing System
43 points – SPiRiT Silver
Need 7 points for SPiRiT Gold
Redesigned System
Uses 17.2% less energy than baseline system
1 point awarded for every 2.5% reduction of energy
6 more points can be obtained, but still need one more…
Goal 5 – Improve Sustainability

## Slide 25: Architectural/Site Breadth Study
Constructed Wetland
Satisfies SPiRiT credit 2.C2 – Innovative use of wastewater technology
Use planting beds of wetland vegetation to treat noxious effluents/sewage
Free water surface – most affordable
Goal 5 – Improve Sustainability
http://www.dep.state.pa.us/Images/

## Slide 26: Architectural/Site Breadth Study
Goal 5 – Improve Sustainability
http://www.unep.org/geo/yearbook/yb2003/images/fresh_img_g_40.jpg

## Slide 27: Architectural/Site Breadth Study
Constructed Wetland
Building uses 24,300 gal/day (max. occupancy)
4300 ft2, 3 ft deep
Adds $38,700 to first cost
Goal 5 – Improve Sustainability
Construction Cost Summary - FWS Constructed Wetland | 
Excavation/Compaction | $8,668.80
Soil/Gravel | $2,786.40
Liner | $12,267.90
Plants | $5,495.40
Plumbing | $9,481.50
Total | $38,700.00

## Slide 28: Architectural/Site Breadth Study
Goal 5 – Improve Sustainability

## Slide 29: Electrical Breadth Study
Goal 3 – Maintain Affordability
Cost of Electrical Additions |  |  |  | 
Added | Qty. | Cost per 100 LF | LF | Total Cost
#10 Wire | 6 | 59.50 | 36 | $129
25 A Breaker | 6 | - | - | $4,074
 |  |  | Total | $4,203
Cost of Electrical Subtractions |  |  |  | 
Subtracted | Qty. | Cost per 100 LF | LF | Total Cost
#3 Wire | 6 | 196.00 | 100 | $1,176
#4 Wire | 12 | 166.50 | 64 | $1,279
#12 Wire | 18 | 47.90 | 128 | $1,104
70 A Breaker | 6 | - | - | $4,818
80 A Breaker | 12 | - | - | $4,818
15 A Breaker | 18 | - | - | $4,074
Panel DP5 | 1 | - | - | $4,000
 |  |  | Total | $21,268
Equipment reduction means power reduction
Panelboard DP5 can be eliminated
Reduces first cost by $17,065
Total cost additions from breadth: $21,635

## Slide 30: Conclusions and Recommendations
Total First Cost of Redesign: $384,050 + $21,635 = $405,685
Total 20-Year Life Cycle Cost Savings: $131,058
  Payback period still only 5.2 years
Owner would pay $109,685 more up-front, but would save $131,058 after 20 years

## Slide 31: Conclusions and Recommendations
Goals Met:
Decrease Space
  YES. DOAS units take up 2% less space than existing AHUs
Increase Energy Efficiency
  YES. Smaller quantity of air to condition; Enthalpy wheel provides energy recovery
Maintain Affordability
  YES. Higher first cost pays back in 5.2 years with savings on energy.
Maintain Occupant Safety
  YES. DOAS takes longer to clear the building, but the building never reaches a critical level.
Improve Sustainability
  YES. 6 credits from mechanical redesign + 1 credit from wetland = 7 credits needed for SPiRiT Gold.

## Slide 32: Acknowledgements
  Project Sponsor: Lou Mittleman
  Dave Casciano
  Todd Garing
  Darren Anderson
  John Morris
  Michael Schwarz
Faculty Advisor: Dr. William Bahnfleth
Justin Bem
Mike Royer
Nick Kutchi
Lou and Julie Ferraro
Brian Hoover

## Slide 33: Questions?
Goals Met:
Decrease Space
  YES. DOAS units take up 2% less space than existing AHUs
Increase Energy Efficiency
  YES. Smaller quantity of air to condition; Enthalpy wheel provides energy recovery
Maintain Affordability
  YES. Higher first cost pays back in 5.2 years with savings on energy.
Maintain Occupant Safety
  YES. DOAS takes longer to clear the building, but the building never reaches a critical level.
Improve Sustainability
  YES. 6 credits from mechanical redesign + 1 credit from wetland = 7 credits needed for SPiRiT Gold.