## dist'n panels
DP4L1
# | ITEM |  | LOAD |  |  | BREAKER |  | FEEDER
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPACE |  |  |  | 100AF/3P
3 |  | SPARE |  |  |  | 225AF/150AT
4 |  | SPARE |  |  |  | 225AF/150AT
5 | DP241 | 208/120 V panel via T5 | 125882.3529 | 0.8 | 436.7681 | 225AF/150AT | a | PRI | 3-#1/0 & 1-#6G, 1½”C
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C
6 | DP231 | 208/120 V panel via T5 | 114852.9412 | 0.8 | 398.4999 | 225AF/150AT | a | PRI | 3-#1/0 & 1-#6G, 1½”C
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C
7 | LCP441 | 480/277 V | 38750 | 0.95 | 49.0621 | 225AF/150AT | a | 10 (150 A)* |  | a
8 | DP221 | 208/120V panel via T5 | 127389.7059 | 0.8 | 49.0621 | 225AF/150AT | a | PRI | 3-#1/0 & 1-#6G, 1½”C
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C
9 | DP211 | 208/120 V panel via T7 | 377815.8916 | 0.8 | 1310.8901 | 400AF/300AT | a | PRI | 3-350 kcmil & 1-#4G, 3”C
[8 empty] | SEC | 4-250 kcmil & 2-#2G, 3”C
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 2244.2822
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP4L2
# | ITEM |  | LOAD |  |  | BREAKER |  | FEEDER
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | LCP421 | 480/277 V | 101625 | 0.95 | 128.6693 | 225AF/150AT | a | 10 (150 A)* |  | a
2 | LCP4L | 480/277 V | 21375 | 0.95 | 27.0633 | 100AF/60AT | a | 2 (60 A)* |  | a
3 | DP212 | 208/120 V panel via T5 | 239063.1466 | 0.8 | 829.4662 | 225AF/150AT | r | PRI | 3-#1/0 & 1-#6G, 1½”C | r
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C | r
4 | DP222 | 208/120 V panel via T5 | 88823.5294 | 0.8 | 308.1868 | 225AF/150AT | r | PRI | 3-#1/0 & 1-#6G, 1½”C | r
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C | r
5 | DP232 | 208/120V panel via T5 | 81029.4118 | 0.8 | 281.1439 | 225AF/150AT | r | PRI | 3-#1/0 & 1-#6G, 1½”C | r
[8 empty] | SEC | 4-250 kcmil & 1-#4G, 3”C | r
6 | DP242 | 208/120V panel via T5 | 102205.8824 | 0.8 | 354.619 | 225AF/150AT | r | 3-#1/0 & 1-#6G, 1½”C 4-250 kcmil & 1-#4G, 3”C |  | a
7 |  | Mech Lift | 5 hp |  |  | 100AF/20AT | a | 4-#12 & 1-#14G, ¾"C |  | a
8 |  | SPARE |  |  |  | 100AF/100AT
9 |  | SPARE |  |  |  | 100AF/100AT
10 |  | SPACE |  |  |  | 100AF/3P
11 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 1929.1485
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP4L3
# | ITEM |  | LOAD |  |  | BREAKER |  | FEEDER
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | CHP-1 | Water Pump | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | r
2 | CHP-2 | Water Pump | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | r
3 | HWP-1 | Water Pump | 15 hp | 0.9 | 46.5633 | 100AF/50AT | a | 3-#8 & 1-#10G, ¾"C |  | a
4 | HWP-2 | Water Pump | 15 hp | 0.9 | 46.5633 | 100AF/50AT | a | 3-#8 & 1-#10G, ¾"C |  | a
5 | PR2L2 | 208/120 V panel via T3 | 15875 | 0.85 | 51.8407 | 100AF/60AT | a | PRI | 3-#4 &1-#10G, 1”C
[8 empty] | SEC | 4-#1 & 1-#8G, 1½”C
6 | MCC4L | Motor Control Center | 38409.9587 | 0.85 | 54.3529 | 100AF/100AT | a | 5 (100 A)* |  | a
7 |  | Trash Compactor |  |  |  | 100AF/30AT |  | 4-#10 & 1-#10G, ¾"C
8 |  | Kitchen Water Heater |  |  |  | 100AF/50AT |  | 4-#6 & 1-#10G, 1"C
9 |  | SPARE |  |  |  | 100AF/20AT
10 |  | Water Booster Pumps |  |  |  | 100AF/20AT
11 |  | SPARE |  |  |  | 100AF/100AT
12 |  | SPACE
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 664.9527
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP2L
# | ITEM |  | LOAD |  |  | BREAKER |  | FEEDER
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | P2L1 | 208/120 V | 26125 | 0.85 | 85.3126 | 225AF/150AT | a | 10 (150 A)* |  | a
2 | P2L2 | 208/120 V | 28831.25 | 0.85 | 94.1501 | 225AF/150AT | a | 10 (150 A)* |  | a
3 | P2L3 | 208/120 V | 37043.75 | 0.85 | 120.9684 | 225AF/150AT | a | 10 (150 A)* |  | a
4 | P2L4 | 208/120 V | 35012.5 | 0.85 | 114.3353 | 225AF/150AT | a | 10 (150 A)* |  | a
5 | PR2L1 | 208/120 V | 12750 | 0.85 | 41.6358 | 100AF/60AT | a | 2 (60 A)* |  | a
6 | D2L1 | 120 V | 4170 |  | 34.75 | 100AF/60AT | a | 1 (60 A)* |  | a
7 | D2L2 | 120 V | 4600 |  | 38.3333 | 100AF/60AT | a | 1 (60 A)* |  | a
8 | D2L3 | 120 V | 4800 |  | 40 | 100AF/60AT | a | 1 (60 A)* |  | a
9 | C2L1 | 120 V | 6030 |  | 50.25 | 100AF/60AT | a | 1 (60 A)* |  | a
10 | C2L2 | 120 V | 5400 |  | 45 | 100AF/60AT | a | 1 (60 A)* |  | a
11 |  | TO RACK 1 (UPS) IN |  |  |  | 225AF/175AT |  | 12 (175 A)* |  | a
12 |  | SERVER ROOM (LL) |  |  |  | 225AF/175AT |  | 12 (175 A)* |  | a
13 |  | SPACE |  |  |  | 100AF/3P
14 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 664.7356
[6 empty] | Main Breaker |  |  | 800AF / 600AT | `
DP211
# | ITEM |  | LOAD |  |  | BREAKER SIZE |  |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a |  | DESIGNED | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPACE |  |  |  | 100AF/3P
3 |  | SPARE |  |  |  | 100AF/100AT
4 |  | SPARE |  |  |  | 100AF/100AT
5 | C2112 | 120 | 5640 | 0.95 | 49.4737 | 100AF/60AT | a | 1 (60 A)* |  | a
6 | C2111 | 120 | 3230 | 0.95 | 28.3333 | 100AF/60AT | a | 1 (60 A)* |  | a
7 | D2114 | 120 | 6350 | 0.95 | 55.7018 | 100AF/60AT | a | 1 (60 A)* |  | a
8 | D2113 | 120 | 7120 | 0.95 | 62.4561 | 100AF/60AT | r | 1 (60 A)* |  | r
9 | D2112 | 120 | 3470 | 0.95 | 30.4386 | 100AF/60AT | a | 1 (60 A)* |  | a
10 | D2111 | 120 | 3660 | 0.95 | 32.1053 | 100AF/60AT | a | 1 (60 A)* |  | a
11 | PR211 | 208/277 V | 29006.25 | 0.85 | 94.7215 | 100AF/100AT | a | 6 (100 A)* |  | a
12 | P2115 | 208/277 V | 63250 | 0.85 | 206.5464 | 225AF/150AT | r | 10 (150 A)* |  | r
13 | P2114 | 208/277 V | 38250 | 0.85 | 124.9075 | 225AF/150AT | a | 10 (150 A)* |  | a
14 | P2113 | 208/277 V | 57031.25 | 0.85 | 186.2387 | 225AF/150AT | r | 10 (150 A)* |  | r
15 | P2112 | 208/277 V | 31375 | 0.85 | 102.4568 | 225AF/150AT | a | 10 (150 A)* |  | a
16 | P2111 | 208/277 V | 23068.75 | 0.85 | 75.3323 | 100AF/100AT | a | 6 (100 A)* |  | a
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 1048.7121
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP212
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | P2121 | 208/277 V | 43968.75 | 0.85 | 143.5824 | 225AF/150AT | a | 10 (150 A)* |  | a
2 | P2122 | 208/277 V | 39125 | 0.85 | 127.7649 | 225AF/150AT | a | 10 (150 A)* |  | a
3 | KP21 | 208/277 V | 51438.75 | 0.85 | 167.9761 | 225AF/150AT | r | 10 (150 A)* |  | r
4 | PR212 | 208/277 V | 27250 | 0.85 | 88.9864 | 225AF/150AT | a | 8 (125 A)* |  | a
5 | D2121 | 120 V | 3780 | 0.95 | 33.1579 | 100AF/60AT | a | 1 (60 A)* |  | a
6 | D2122 | 120 V | 3780 | 0.95 | 33.1579 | 100AF/60AT | a | 1 (60 A)* |  | a
7 | C2121 | 120 V | 2280 | 0.95 | 20 | 100AF/60AT | a | 1 (60 A)* |  | a
8 | C2122 | 120 V | 5580 | 0.95 | 48.9474 | 100AF/100AT | a | 1 (60 A)* |  | a
9 |  | Mech Lift |  |  |  | 100AF/20AT |  |  |  | a
10 |  | SPARE |  |  |  | 100AF/100AT
11 |  | SPACE |  |  |  | 100AF/3P
12 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 663.5729
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP221
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPACE |  |  |  | 100AF/3P
3 |  | SPARE |  |  |  | 100AF/100AT
4 |  | SPARE |  |  |  | 100AF/100AT
5 | PR221 | 208/277 V | 3750 | 0.85 | 12.2458 | 100AF/100AT | a | 6 (100 A)* |  | a
6 | P2214 | 208/277 V | 29625 | 0.85 | 96.7421 | 225AF/150AT | a | 10 (150 A)* |  | a
7 | P2213 | 208/277 V | 18750 | 0.85 | 61.2292 | 100AF/100AT | a | 6 (100 A)* |  | a
8 | P2212 | 208/277 V | 31062.5 | 0.85 | 101.4363 | 225AF/150AT | a | 10 (150 A)* |  | a
9 | P2211 | 208/277 V | 25093.75 | 0.85 | 81.945 | 225AF/150AT | a | 10 (150 A)* |  | a
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 353.5985
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP222
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | P2221 | 208/120 V | 19500 | 0.85 | 63.6783 | 100AF/100AT | a | 6 (100 A)* |  | a
2 | P2222 | 208/120 V | 22875 | 0.85 | 74.6996 | 100AF/100AT | a | 6 (100 A)* |  | a
3 | P2223 | 208/120 V | 28250 | 0.85 | 92.252 | 100AF/100AT | a | 6 (100 A)* |  | a
4 | PR222 | 208/120 V | 4875 | 0.85 | 15.9196 | 100AF/100AT | a | 6 (100 A)* |  | a
5 |  | SPARE |  |  |  | 100AF/100AT
6 |  | SPARE |  |  |  | 100AF/100AT
7 |  | SPACE |  |  |  | 100AF/3P
8 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 246.5495
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP231
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPACE |  |  |  | 100AF/3P
3 |  | SPARE |  |  |  | 100AF/100AT
4 |  | SPARE |  |  |  | 100AF/100AT
5 | PR231 | 208/277 V | 12750 | 0.85 | 41.6358 | 100AF/100AT | a | 6 (100 A)* |  | a
6 | P2314 | 208/277 V | 20750 | 0.85 | 67.7603 | 100AF/100AT | a | 6 (100 A)* |  | a
7 | P2313 | 208/277 V | 26375 | 0.85 | 86.129 | 225AF/150AT | a | 10 (150 A)* |  | a
8 | P2312 | 208/277 V | 13875 | 0.85 | 45.3096 | 100AF/100AT | a | 6 (100 A)* |  | a
9 | P2311 | 208/277 V | 23875 | 0.85 | 77.9651 | 100AF/100AT | a | 6 (100 A)* |  | a
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 318.7999
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP232
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | P2321 | 208/277 V | 16625 | 0.85 | 54.2899 | 100AF/100AT | a | 6 (100 A)* |  | a
2 | P2322 | 208/277 V | 22125 | 0.85 | 72.2504 | 100AF/100AT | a | 6 (100 A)* |  | a
3 | P2323 | 208/277 V | 16000 | 0.85 | 52.2489 | 100AF/100AT | a | 6 (100 A)* |  | a
4 | PR232 | 208/277 V | 14125 | 0.85 | 46.126 | 100AF/100AT | a | 6 (100 A)* |  | a
5 |  | SPARE |  |  |  | 100AF/100AT
6 |  | SPARE |  |  |  | 100AF/100AT
7 |  | SPACE |  |  |  | 100AF/3P
8 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 224.9152
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP241
# | ITEM |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPACE |  |  |  | 100AF/3P
3 |  | SPARE |  |  |  | 100AF/100AT
4 | P2P1 | 208/277 V | 14500 | 0.85 | 47.3506 | 100AF/60AT | a | 2 (60 A)* |  | a
5 | PR241 | 208/277 V | 6250 | 0.85 | 20.4097 | 100AF/100AT | a | 6 (100 A)* |  | a
6 | P2414 | 208/277 V | 18625 | 0.85 | 60.821 | 100AF/100AT | a | 6 (100 A)* |  | a
7 | P2413 | 208/277 V | 26625 | 0.85 | 86.9454 | 225AF/150AT | a | 10 (150 A)* |  | a
8 | P2412 | 208/277 V | 15375 | 0.85 | 50.2079 | 100AF/100AT | a | 6 (100 A)* |  | a
9 | P2411 | 208/277 V | 25625 | 0.85 | 83.6799 | 100AF/100AT | a | 6 (100 A)* |  | a
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 349.4145
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP242
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | P2421 | 208/277 V | 17125 | 0.85 | 55.9226 | 100AF/100AT | a | 6 (100 A)* |  | a
2 | P2422 | 208/277 V | 21875 | 0.85 | 71.434 | 100AF/100AT | a | 6 (100 A)* |  | a
3 | P2423 | 208/277 V | 24125 | 0.85 | 78.7815 | 100AF/100AT | a | 6 (100 A)* |  | a
4 | PR242 | 208/277 V | 10500 | 0.85 | 34.2883 | 100AF/100AT | a | 6 (100 A)* |  | a
5 | P2P2 | 208/277 V | 13250 | 0.85 | 43.2686 | 100AF/60AT | a | 2 (60 A)* |  | a
6 |  | SPARE |  |  |  | 100AF/100AT
7 |  | SPACE |  |  |  | 100AF/3P
8 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 283.6952
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP4P1
# | ITEM |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | RF-1 | Fan | 30 hp | 0.9 | 93.1265 | 100AF/90AT | r | 3-#4 & 1-#6G, 1"C |  | a
2 | RF-2 | Fan | 15 hp | 0.9 | 46.5633 | 100AF/50AT | a | 3-#8 & 1-#10G, ¾"C |  | a
3 | RF-3 | Fan | 30 hp | 0.9 | 93.1265 | 100AF/90AT | r | 3-#4 & 1-#6G, 1"C |  | a
4 | RF-4 | Fan | 30 hp | 0.9 | 93.1265 | 100AF/90AT | r | 3-#4 & 1-#6G, 1"C |  | a
5 | RF-5 | Fan | 30 hp | 0.9 | 93.1265 | 100AF/90AT | r | 3-#4 & 1-#6G, 1"C |  | a
6 |  | SPARE |  |  |  | 100AF/20AT
7 | AHU-A | Air Handling Unit | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | a
8 | AHU-B | Air Handling Unit | 40 hp | 0.9 | 124.1687 | 225AF/125AT | a | 3-#3 & 1-#6G, 1¼"C |  | a
9 | AHU-C | Air Handling Unit | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | a
10 | AHU-D | Air Handling Unit | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | a
11 | AHU-E | Air Handling Unit | 75 hp | 0.9 | 232.8163 | 225AF/200AT | r | 3-#2/0 & 1-#4G, 2"C |  | a
12 |  | SPARE |  |  |  | 100AF/60AT
13 | EX-9 | Fan | 1.5 hp | 0.9 | 2.235 | 100AF/20AT | a | 3-#12 & 1-#12G, ¾"C |  | a
14 | EX-8 | Fan | 2.5 hp | 0.9 | 7.7605 | 100AF/20AT | a | 3-#12 & 1-#12G, ¾"C |  | a
15 |  | SPARE |  |  |  | 100AF/100AT
16 |  | SPARE |  |  |  | 100AF/100AT
17 |  | SPACE |  |  |  | 100AF/3P
18 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 1484.4988
[6 empty] | Main Breaker |  |  | 800AF / 600AT
DP4P2
# | ITEM |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCTD | PF | A | DESIGNED | a | DESIGNED |  | a
1 | AHU-F | Air Handling Unit | 40 hp | 0.9 | 124.1687 | 225AF/125AT | a | 3-#3 & 1-#6G, 1¼"C |  | a
2 | AHU-G | Air Handling Unit | 50 hp | 0.9 | 155.2109 | 225AF/150AT | a | 3-#1 & 1-#6G, 1½"C |  | a
3 | AHU-H | Air Handling Unit | 50 hp | 0.9 | 155.2109 | 225AF/150AT | r | 3-#1 & 1-#6G, 1½"C |  | r
4 | AHU-I | Air Handling Unit | 50 hp | 0.9 | 155.2109 | 225AF/150AT | r | 3-#1 & 1-#6G, 1½"C |  | r
5 | AHU-J | Air Handling Unit | 20 hp | 0.9 | 62.0843 | 225AF/60AT | a | 3-#6 & 1-#8G, ¾"C |  | a
6 | RF-6 | Fan | 20 hp | 0.9 | 62.0843 | 100AF/60AT | a | 3-#6 & 1-#8G, ¾"C |  | a
7 | EX-7 | Fan | 2.5 hp | 0.9 | 7.7605 | 100AF/20AT | a | 3-#12 & 1-#12G, ¾"C |  | a
8 | RF-8 | Fan | 25 hp | 0.9 | 77.6054 | 100AF/70AT | a | 3-#6 & 1-#8G, ¾"C |  | a
9 | RF-9 | Fan | 25 hp | 0.9 | 77.6054 | 100AF/70AT | a | 3-#6 & 1-#8G, ¾"C |  | a
10 | RF-10 | Fan | 10 hp | 0.9 | 31.0422 | 100AF/30AT | a | 3-#10 & 1-#10G, ¾"C |  | a
11 |  | SPARE |  |  |  | 100AF/100AT
12 | EX-4 | Fan | 5 | 0.9 | 15.5211 | 100AF/20AT | a | 4-#12 & 1-#12G, ¾"C |  | a
13 | EX-10 | Fan | 1.5 hp | 0.9 | 2.235 | 100AF/20AT | a | 3-#12 & 1-#12G, ¾"C |  | a
14 |  | SPARE |  |  |  | 100AF/20AT
15 |  | SPARE |  |  |  | 100AF/100AT
16 |  | SPACE |  |  |  | 100AF/3P
17 |  | SPACE |  |  |  | 100AF/3P
[6 empty] | TYPE |  |  |  | a
[6 empty] | Total Load |  |  | 925.7397
[6 empty] | Main Breaker |  |  | 800AF / 600AT
MDPEM4L |  | 480/277V, 3∅, 4W, 225A, 65KAIC
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CON | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE
2 |  | SPACE
3 |  | SPARE
4 |  | SPARE
5 | PEM2L | 208/120 V panel via T4 | 10600 | 0.85 | 14.9998 | 100AF/80AT | a | PRI | 3-#3 & 1-#8G, 1¼”C | a
[8 empty] | SEC | 4-#1/0 & 1-#6G, 2”C
6 | PEM41 | 480/277 V | 55900 | 0.85 | 79.1026 | 100AF/100AT | a | 6 (100 A)* |  | a
7 | PEM44 | 480/277 V | 42000 | 0.85 | 59.4331 | 100AF/100AT | a | 6 (100 A)* |  | a
TYPE |  | DESIGNED |  |  |  | CALCULATED
Total Load |  | 153.5355 | [7 empty] | a
Transformer |  | 75 kVA, 4160/480-277V, 3∅ | [7 empty] | r
Feeder |  | 10 (XFMR-ATS) / 18 (ATS-MDPEM4L) | [7 empty] | r
Main Breaker |  | 150A/3P | [7 empty] | a
FEEDER | [9 empty] | a
MDPLR4L
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CONNCT'D | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE |  |  |  | 100AF/3P
2 |  | SPARE |  |  |  | 100AF/100AT
3 |  | Elevator #1 |  |  |  | 225AF/150AT |  | 9 (150 A)**
4 |  | Elevator #2 |  |  |  | 225AF/150AT |  | 9 (150 A)**
5 |  | Elevator #3 |  |  |  | 225AF/150AT |  | 9 (150 A)**
6 |  | SPARE |  |  |  | 100AF/20AT
7 |  | SPARE |  |  |  | 100AF/80AT
8 | DPLR2L | Panel via T4 | 72600 | 0.85 | 278.9169 | 100AF/80AT | a | PRI | 3-#3 & 1-#8G, 1¼”C | a
[8 empty] | SEC | 4-#1/0 & 1-#6G, 2”C
9 | RF-7 | Smoke Evacuation Fan | 30 hp | 0.9 | 93.1265 | 100AF/90AT | r | 3#4 & 1#6G - 1"C |  | a
TYPE |  | DESIGNED |  |  |  | CALCULATED
Total Load |  | 372.0434 | [7 empty] | a
Transformer |  | 150 kVA, 4160/480-277V, 3∅ | [7 empty] | r
Feeder | [9 empty] | a
Main Breaker | [9 empty] | r
Panel |  | 480/277V, 3∅, 3W, 400A, 65KAIC | [7 empty] | a
DPLR2L |  | 208/120V, 3∅, 4W, 10kAIC
# | DIRECTORY |  | LOAD |  |  | BREAKER SIZE |  | FEEDER SIZE
| TAG | DESCRIPTION | CON | PF | A | DESIGNED | a | DESIGNED |  | a
1 |  | SPACE
2 |  | SPACE
3 |  | SPARE
4 | PLR24 | 208/120 V | 16000 | 0.85 | 52.2489 |  | r | 2 (60 A)* |  | r
5 | PLR21 | 208/120 V | 29000 | 0.85 | 94.7011 |  | a | 6 (100 A)* |  | a
6 | PLR2L | 208/120 V | 27600 | 0.85 | 90.1293 |  | a | 6 (100 A)* |  | a
CALCULATED
TOTAL LOAD |  | 237.0794 | [7 empty] | a
XMFR |  | T4 | [7 empty] | r
MAIN BKR |  | 250AF/150AT | [7 empty] | r
Panel | [9 empty] | a

## indiv. panels
PANEL | VOLTAGE | LTG [VA] | RECEPTACLE |  | EQUIPMENT |  | SPARE | TOTAL LOADS |  |  |  | PANEL | VOLTAGE | LTG | REC | EQUIP'T | PANEL LOAD | TOTAL LOADS
|  |  | CONCT'D | DEMAND | CONCT'D | DEMAND |  | TOT LOAD | DEMAND | PANEL | AMPS | [6 empty] | CONCT'D | DEMAND | PANEL | AMPS
[12 empty] | PLR2L | 208/120 | -- | 16000 | #REF! | #REF!
LCP4L | 480/277 | 17100 | 0 | 0 | 0 | 0 | 0 | 17100 | 17100 | 21375 | 25.7101 | PLR2L | 208/120 | 0 | 27600 |  | 27600 | 55200 | 27600 | 34500 | 95.7624
LCP411 | 480/277 | 31000 | 0 | 0 | 0 | 0 | 0 | 31000 | 31000 | 38750 | 46.609 | PLR21 | 208/120 | 0 | 3600 | 25400 | 29000 | 32600 | 54400 | 68000 | 188.7491
LCP421 | 480/277 | 78300 | 0 | 0 | 0 | 0 | 3000 | 81300 | 81300 | 101625 | 122.2359 | PLR24 | 208/120 | 0 | 0 | 16000 | 16000 | 16000 | 32000 | 40000 | 111.0289
LCP431 | 480/277 | 52900 | 0 | 0 | 0 | 0 | 0 | 52900 | 52900 | 66125 | 79.536 | PEM41 | 480/277 | 55900 | 0 | 0 | 55900 | 55900 | 111800 | 139750 | 387.9072
LCP441 | 480/277 | 57200 | 0 | 0 | 0 | 0 | 0 | 57200 | 57200 | 71500 | 86.0011 | PEM44 | 480/277 | 42000 | 0 | 0 | 42000 | 42000 | 84000 | 105000 | 291.4509
KP21 | 208/120 | 1600 | 55102 | 32551 | 14000 | 7000 | 0 | 70702 | 41151 | 51438.75 | 142.7797 | PEM2L | 208/120 | 10600 | 0 | 0 | 10600 | 10600 | 21200 | 26500 | 73.5566
P2111 | 208/120 | 0 | 25510 | 17755 | 1400 | 700 | 0 | 26910 | 18455 | 23068.75 | 64.0324 | PEM211 | 208/120 | 13600 | 0 | 0 | 13600 | 13600 | 27200 | 34000 | 94.3746
P2112 | 208/120 | 0 | 37600 | 23800 | 2600 | 1300 | 0 | 40200 | 25100 | 31375 | 87.0883 | TOTALS |  | 122100 | 47200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
P2113 | 208/120 | 0 | 60150 | 35075 | 9100 | 4550 | 6000 | 75250 | 45625 | 57031.25 | 158.3029 | [6 empty] | 0 | 0 | 0 | 0
P2114 | 208/120 | 0 | 40800 | 25400 | 10400 | 5200 | 0 | 51200 | 30600 | 38250 | 106.1714 | [6 empty] | 0 | 0 | 0 | 0
P2115 | 208/120 | 0 | 84800 | 47400 | 6400 | 3200 | 0 | 91200 | 50600 | 63250 | 175.5644 | [6 empty] | 0 | 0 | 0 | 0
P2121 | 208/120 | 0 | 50150 | 30075 | 10200 | 5100 | 0 | 60350 | 35175 | 43968.75 | 122.045 | [6 empty] | 0 | 0 | 0 | 0
P2122 | 208/120 | 0 | 47000 | 28500 | 5600 | 2800 | 0 | 52600 | 31300 | 39125 | 108.6001 | [6 empty] | 0 | 0 | 0 | 0
P2211 | 208/120 | 0 | 28150 | 19075 | 2000 | 1000 | 0 | 30150 | 20075 | 25093.75 | 69.6533 | [6 empty] | 0 | 0 | 0 | 0
P2212 | 208/120 | 2000 | 31100 | 20550 | 4600 | 2300 | 0 | 37700 | 24850 | 31062.5 | 86.2209 | [6 empty] | 0 | 0 | 0 | 0
P2213 | 208/120 | 1200 | 15600 | 12800 | 2000 | 1000 | 0 | 18800 | 15000 | 18750 | 52.0448 | [6 empty] | 0 | 0 | 0 | 0
P2214 | 208/120 | 0 | 36000 | 23000 | 1400 | 700 | 0 | 37400 | 23700 | 29625 | 82.2308 | [6 empty] | 0 | 0 | 0 | 0
P2221 | 208/120 | 0 | 19200 | 14600 | 2000 | 1000 | 0 | 21200 | 15600 | 19500 | 54.1266 | [6 empty] | 0 | 0 | 0 | 0
P2222 | 208/120 | 1200 | 21400 | 15700 | 2800 | 1400 | 0 | 25400 | 18300 | 22875 | 63.4947 | [6 empty] | 0 | 0 | 0 | 0
P2223 | 208/120 | 1200 | 28200 | 19100 | 4600 | 2300 | 0 | 34000 | 22600 | 28250 | 78.4142 | [6 empty] | 0 | 0 | 0 | 0
P2311 | 208/120 | 400 | 25400 | 17700 | 2000 | 1000 | 0 | 27800 | 19100 | 23875 | 66.2704 | [6 empty] | 0 | 0 | 0 | 0
P2312 | 208/120 | 0 | 12200 | 11100 | 0 | 0 | 0 | 12200 | 11100 | 13875 | 38.5131 | [6 empty] | 0 | 0 | 0 | 0
P2313 | 208/120 | 0 | 32200 | 21100 | 0 | 0 | 0 | 32200 | 21100 | 26375 | 73.2097 | [6 empty] | 0 | 0 | 0 | 0
P2314 | 208/120 | 1200 | 20400 | 15200 | 400 | 200 | 0 | 22000 | 16600 | 20750 | 57.5962 | [6 empty] | 0 | 0 | 0 | 0
P2321 | 208/120 | 0 | 16600 | 13300 | 0 | 0 | 0 | 16600 | 13300 | 16625 | 46.1464 | [6 empty] | 0 | 0 | 0 | 0
P2322 | 208/120 | 800 | 22000 | 16000 | 1800 | 900 | 0 | 24600 | 17700 | 22125 | 61.4129 | [6 empty] | 0 | 0 | 0 | 0
P2323 | 208/120 | 0 | 14000 | 12000 | 1600 | 800 | 0 | 15600 | 12800 | 16000 | 44.4116 | [6 empty] | 0 | 0 | 0 | 0
P2411 | 208/120 | 0 | 31000 | 20500 | 0 | 0 | 0 | 31000 | 20500 | 25625 | 71.1279 | [6 empty] | 0 | 0 | 0 | 0
P2412 | 208/120 | 0 | 14600 | 12300 | 0 | 0 | 0 | 14600 | 12300 | 15375 | 42.6767 | [6 empty] | 0 | 0 | 0 | 0
P2413 | 208/120 | 0 | 32600 | 21300 | 0 | 0 | 0 | 32600 | 21300 | 26625 | 73.9036 | [6 empty] | 0 | 0 | 0 | 0
P2414 | 208/120 | 0 | 19800 | 14900 | 0 | 0 | 0 | 19800 | 14900 | 18625 | 51.6978 | [6 empty] | 0 | 0 | 0 | 0
P2421 | 208/120 | 0 | 17400 | 13700 | 0 | 0 | 0 | 17400 | 13700 | 17125 | 47.5342 | [6 empty] | 0 | 0 | 0 | 0
P2422 | 208/120 | 0 | 25000 | 17500 | 0 | 0 | 0 | 25000 | 17500 | 21875 | 60.7189 | [6 empty] | 0 | 0 | 0 | 0
P2423 | 208/120 | 0 | 28600 | 19300 | 0 | 0 | 0 | 28600 | 19300 | 24125 | 66.9643 | [6 empty] | 0 | 0 | 0 | 0
P2L1 | 208/120 | 0 | 30400 | 20200 | 1400 | 700 | 0 | 31800 | 20900 | 26125 | 72.5157 | [6 empty] | 0 | 0 | 0 | 0
P2L2 | 208/120 | 0 | 29130 | 19565 | 7000 | 3500 | 0 | 36130 | 23065 | 28831.25 | 80.0275 | [6 empty] | 0 | 0 | 0 | 0
P2L3 | 208/120 | 0 | 44070 | 27035 | 3600 | 1800 | 800 | 48470 | 29635 | 37043.75 | 102.8232 | [6 empty] | 0 | 0 | 0 | 0
P2L4 | 208/120 | 0 | 41220 | 25610 | 4800 | 2400 | 0 | 46020 | 28010 | 35012.5 | 97.185 | [6 empty] | 0 | 0 | 0 | 0
P2P1 | 208/120 | 0 | 13200 | 11600 | 0 | 0 | 0 | 13200 | 11600 | 14500 | 40.248 | [6 empty] | 0 | 0 | 0 | 0
P2P2 | 208/120 | 6000 | 4400 | 4400 | 400 | 200 | 0 | 10800 | 10600 | 13250 | 36.7783 | [6 empty] | 0 | 0 | 0 | 0
PR211 | 208/120 | 0 | 35010 | 22505 | 1400 | 700 | 0 | 36410 | 23205 | 29006.25 | 80.5133 | [6 empty] | 0 | 0 | 0 | 0
PR212 | 208/120 | 0 | 28000 | 19000 | 5600 | 2800 | 0 | 33600 | 21800 | 27250 | 75.6384 | [6 empty] | 0 | 0 | 0 | 0
PR221 | 208/120 | 0 | 2000 | 2000 | 2000 | 1000 | 0 | 4000 | 3000 | 3750 | 10.409 | [6 empty] | 0 | 0 | 0 | 0
PR222 | 208/120 | 0 | 3000 | 3000 | 1800 | 900 | 0 | 4800 | 3900 | 4875 | 13.5316 | [6 empty] | 0 | 0 | 0 | 0
PR231 | 208/120 | 0 | 9400 | 9400 | 1600 | 800 | 0 | 11000 | 10200 | 12750 | 35.3905 | [6 empty] | 0 | 0 | 0 | 0
PR232 | 208/120 | 0 | 11000 | 10500 | 1600 | 800 | 0 | 12600 | 11300 | 14125 | 39.2071 | [6 empty] | 0 | 0 | 0 | 0
PR241 | 208/120 | 0 | 5000 | 5000 | 0 | 0 | 0 | 5000 | 5000 | 6250 | 17.3483 | [6 empty] | 0 | 0 | 0 | 0
PR242 | 208/120 | 0 | 8400 | 8400 | 0 | 0 | 0 | 8400 | 8400 | 10500 | 29.1451 | [6 empty] | 0 | 0 | 0 | 0
PR2L1 | 208/120 | 0 | 10400 | 10200 | 0 | 0 | 0 | 10400 | 10200 | 12750 | 35.3905 | [6 empty] | 0 | 0 | 0 | 0
PR2L2 | 208/120 | 0 | 14600 | 12300 | 800 | 400 | 0 | 15400 | 12700 | 15875 | 44.0646 | [6 empty] | 0 | 0 | 0 | 0
C2L1 | 120 | 6030 | 0 | 0 | 0 | 0 | 0 | 6030 | 6030 | 7537.5 | 20.922 | [6 empty] | 0 | 0 | 0 | 0
C2L2 | 120 | 5400 | 0 | 0 | 0 | 0 | 0 | 5400 | 5400 | 6750 | 18.7361 | [6 empty] | 0 | 0 | 0 | 0
C2111 | 120 | 3230 | 0 | 0 | 0 | 0 | 0 | 3230 | 3230 | 4037.5 | 11.207 | [6 empty] | 0 | 0 | 0 | 0
C2112 | 120 | 5640 | 0 | 0 | 0 | 0 | 0 | 5640 | 5640 | 7050 | 19.5688 | [6 empty] | 0 | 0 | 0 | 0
C2121 | 120 | 2280 | 0 | 0 | 0 | 0 | 0 | 2280 | 2280 | 2850 | 7.9108 | [6 empty] | 0 | 0 | 0 | 0
C2122 | 120 | 5580 | 0 | 0 | 0 | 0 | 0 | 5580 | 5580 | 6975 | 19.3607 | [6 empty] | 0 | 0 | 0 | 0
D2L1 | 120 | 4170 | 0 | 0 | 0 | 0 | 0 | 4170 | 4170 | 5212.5 | 43.4375 | [6 empty] | 0 | 0 | 0 | 0
D2L2 | 120 | 4600 | 0 | 0 | 0 | 0 | 0 | 4600 | 4600 | 5750 | 47.9167 | [6 empty] | 0 | 0 | 0 | 0
D2L3 | 120 | 4800 | 0 | 0 | 0 | 0 | 0 | 4800 | 4800 | 6000 | 50 | [6 empty] | 0 | 0 | 0 | 0
D2121 | 120 | 3780 | 0 | 0 | 0 | 0 | 0 | 3780 | 3780 | 4725 | 39.375 | [6 empty] | 0 | 0 | 0 | 0
D2122 | 120 | 3780 | 0 | 0 | 0 | 0 | 0 | 3780 | 3780 | 4725 | 39.375 | [6 empty] | 0 | 0 | 0 | 0
D2111 | 120 | 3660 | 0 | 0 | 0 | 0 | 0 | 3660 | 3660 | 4575 | 38.125 | [6 empty] | 0 | 0 | 0 | 0
D2112 | 120 | 3470 | 0 | 0 | 0 | 0 | 0 | 3470 | 3470 | 4337.5 | 36.1458 | [6 empty] | 0 | 0 | 0 | 0
D2113 | 120 | 7120 | 0 | 0 | 0 | 0 | 0 | 7120 | 7120 | 8900 | 74.1667 | [6 empty] | 0 | 0 | 0 | 0
D2114 | 120 | 6350 | 0 | 0 | 0 | 0 | 0 | 6350 | 6350 | 7937.5 | 66.1458 | [6 empty] | 0 | 0 | 0 | 0
|  | 321990 |  |  |  |  | TOTALS | 1630.482 | 1192.236 | 1490.295 | 3955.6544 | [6 empty] | #REF! | #REF! |  | 0

## mech loads
AIR HANDLING UNITS (CHW)
EQUIPMENT TYPE | TAG | VOLTS | PHASE | HZ | MHP | TOTAL LOAD
[6 empty] | kW | kVA | AMPS
Air Handling Unit (CHW) | AHU-A | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| AHU-B | 480 | 3 | 60 | 40 | 53.6409 | 59.601 | 124.1687
| AHU-C | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| AHU-D | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| AHU-E | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| AHU-F | 480 | 3 | 60 | 40 | 53.6409 | 59.601 | 124.1687
| AHU-G | 480 | 3 | 60 | 50 | 67.0511 | 74.5012 | 155.2109
| AHU-H | 480 | 3 | 60 | 50 | 67.0511 | 74.5012 | 155.2109
| AHU-I | 480 | 3 | 60 | 50 | 67.0511 | 74.5012 | 155.2109
| AHU-J | 480 | 3 | 60 | 20 | 26.8204 | 29.8005 | 62.0843
| FANS | [6 empty] | #DIV/0!
| TAG | VOLTS | PHASE | HZ | MHP | TOTAL LOAD |  | #VALUE!
[6 empty] | kW | kVA | #VALUE!
Fan | RF-1 | 480 | 3 | 60 | 30 | 40.2307 | 44.7007 | 93.1265
| RF-2 | 480 | 3 | 60 | 15 | 20.1153 | 22.3504 | 46.5633
| RF-3 | 480 | 3 | 60 | 30 | 40.2307 | 44.7007 | 93.1265
| RF-4 | 480 | 3 | 60 | 30 | 40.2307 | 44.7007 | 93.1265
| RF-5 | 480 | 3 | 60 | 30 | 40.2307 | 44.7007 | 93.1265
| RF-6 | 480 | 3 | 60 | 20 | 26.8204 | 29.8005 | 62.0843
| RF-7 | 480 | 3 | 60 | 30 | 40.2307 | 44.7007 | 93.1265
| RF-8 | 480 | 3 | 60 | 25 | 33.5255 | 37.2506 | 77.6054
| RF-9 | 480 | 3 | 60 | 25 | 33.5255 | 37.2506 | 77.6054
| RF-10 | 480 | 3 | 60 | 10 | 13.4102 | 14.9002 | 31.0422
| EX-3 | 480 | 3 | 60 | 10 | 13.4102 | 14.9002 | 31.0422
| EX-4 | 480 | 3 | 60 | 5 | 6.7051 | 7.4501 | 15.5211
| EX-7 | 480 | 3 | 60 | 2.5 | 3.3526 | 3.7251 | 7.7605
| EX-8 | 480 | 3 | 60 | 2.5 | 3.3526 | 3.7251 | 7.7605
| SF-1 | 480 | 3 | 60 | 5 | 6.7051 | 7.4501 | 15.5211
| PACKAGED HEATING/VENTILATING UNITS | [6 empty] | #DIV/0!
| TAG | VOLTS | PHASE | HZ | MHP (FAN) | TOTAL LOAD |  | #VALUE!
[6 empty] | kW | kVA | #VALUE!
Packaged Heating/Ventilating Unit | HVU-1 | 460 | 3 | 60 | 5 | 6.7051 | 7.4501 | 16.1959
| HVU-2a | 460 | 3 | 60 | 5 | 6.7051 | 7.4501 | 16.1959
| HVU-2b | 460 | 3 | 60 | 5 | 6.7051 | 7.4501 | 16.1959
| WATER PUMPS | [6 empty] | #DIV/0!
| TAG | VOLTS | PHASE | HZ | MHP | TOTAL LOAD |  | #VALUE!
[6 empty] | kW | kVA | #VALUE!
Water Pump | CHP-1 | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| CHP-2 | 480 | 3 | 60 | 75 | 100.5766 | 111.7518 | 232.8163
| HWP-1 | 480 | 3 | 60 | 15 | 20.1153 | 22.3504 | 46.5633
| HWP-2 | 480 | 3 | 60 | 15 | 20.1153 | 22.3504 | 46.5633
| HWP-3 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| HWP-4 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| HWP-5 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| HWP-6 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| HWP-7 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| HWP-8 | 480 | 3 | 60 | 1 ½ | 2.0115 | 2.235 | 4.6563
| CABINET & UNIT HEATERS | [6 empty] | #DIV/0!
| TAG | VOLTS | PHASE | HZ | MHP | TOTAL LOAD |  | #VALUE!
[6 empty] | kW | kVA | #VALUE!
Cabinet & Unit Heater | CUH-1 | 120 | 1 | 60 | 0.16667 | 0.2235 | 0.26295 | 2.1912
| CUH-2 | 120 | 1 | 60 | 0.16667 | 0.2235 | 0.26295 | 2.1912
| UH-1 | 120 | 1 | 60 | 0.16667 | 0.2235 | 0.26295 | 2.1912
| CUH-3 | 120 | 1 | 60 | 0.16667 | 0.2235 | 0.26295 | 2.1912
FAN COIL UNITS
EQUIPMENT TYPE | TAG | VOLTS | PHASE | HZ | AMPS | TOTAL LOAD
[6 empty] | kW | kVA
Fan Coil Unit | FCU-1 | 115 | 1 | 60 | 1.7 | 0.16617 | 0.1955 | 1.7
| FCU-2 | 115 | 1 | 60 | 2.1 | 0.20527 | 0.2415 | 2.1
| FCU-3 | 115 | 1 | 60 | 1/2 HP | 0.67051 | 0.78884 | 6.8594
| FCU-4 | 115 | 1 | 60 | 1 HP | 1.341 | 1.5777 | 13.7189
| FCU-5 | 115 | 1 | 60 | 1/2 HP | 0.67051 | 0.78884 | 6.8594
| FCU-6 | 115 | 1 | 60 | 2.6 | 0.25415 | 0.299 | 2.6

## MCC
| TAG | HP | KW | FLA
1 | HWP-3 | 1.5 |  | 3
2 | HWP-4 | 1.5 |  | 3
3 | HWP-5 | 1.5 |  | 3
4 | HWP-6 | 1.5 |  | 3
5 | HWP-7 | 1.5 |  | 3
6 | HWP-8 | 1.5 |  | 3
7 | HV-1 | 5 |  | 7.6
8 | EX-3 | 10 |  | 13
9 | SF-1 | 5 |  | 7.6
10 | SPARE | 15 |  | -
11 | SPACE | - |  | -
12 | SPACE | - |  | -
|  |  | TOTAL | 46.2

## dim-cntl panel loads
| D2111 | LOAD [VA] |  | D2112 | LOAD [VA] |  | D2113 | LOAD [VA] |  | D2114 | LOAD [VA]
1 |  | 520 | 1 |  | 440 | 1 |  | 520 | 1 |  | 800
2 |  | 400 | 2 |  | 100 | 2 |  | 400 | 2 |  | 800
3 |  | 100 | 3 |  | 100 | 3 |  | 100 | 3 |  | 800
4 |  | 100 | 4 |  | 100 | 4 |  | 100 | 4 |  | 800
5 |  | 100 | 5 |  | 50 | 5 |  | 100 | 5 |  | 200
6 |  |  | 6 |  |  | 6 |  |  | 6 |  | 50
7 |  |  | 7 |  |  | 7 |  |  | 7 |  | 200
8 |  |  | 8 |  |  | 8 |  |  | 8 |  | 200
9 |  | 520 | 9 |  | 440 | 9 |  | 150 | 9
10 |  | 400 | 10 |  | 100 | 10 |  | 50 | 10 |  | 1000
11 |  | 100 | 11 |  | 100 | 11 |  | 150 | 11 |  | 1000
12 |  | 100 | 12 |  | 100 | 12 |  | 600 | 12 |  | 500
13 |  | 100 | 13 |  |  | 13 |  |  | 13
14 |  | 100 | 14 |  |  | 14 |  | 50 | 14
15 |  | 100 | 15 |  | 600 | 15 |  | 50 | 15
16 |  | 100 | 16 |  |  | 16 |  | 1250 | 16
17 |  | 720 | 17 |  | 440 | 17 |  | 100 | 17
18 |  | 50 | 18 |  | 100 | 18 |  | 100 | 18
19 |  | 100 | 19 |  | 100 | 19 |  | 100 | 19
20 |  | 50 | 20 |  | 100 | 20 |  | 100 | 20
21 |  |  | 21 |  |  | 21 |  | 1000 | 21
22 |  |  | 22 |  |  | 22 |  | 1000 | 22
23 |  |  | 23 |  | 600 | 23 |  | 1000 | 23
24 |  |  | 24 |  |  | 24 |  | 200 | 24
|  | 3660 |  |  | 3470 |  |  | 7120 |  |  | 6350
| C2111 | LOAD [VA] |  | C2112 | LOAD [VA] |  | C2121 | LOAD [VA] |  | C2122 | LOAD [VA]
1 |  |  | 1 |  | 600 | 1 |  |  | 1 |  | 600
2 |  | 120 | 2 |  | 160 | 2 |  | 400 | 2 |  | 300
3 |  | 120 | 3 |  | 40 | 3 |  | 120 | 3 |  | 120
4 |  | 120 | 4 |  | 160 | 4 |  | 120 | 4 |  | 120
5 |  | 400 | 5 |  | 120 | 5 |  | 120 | 5 |  | 120
6 |  |  | 6 |  | 600 | 6 |  |  | 6 |  | 600
7 |  | 120 | 7 |  | 600 | 7 |  |  | 7 |  | 600
8 |  | 120 | 8 |  | 160 | 8 |  | 400 | 8 |  | 300
9 |  | 120 | 9 |  | 40 | 9 |  | 120 | 9 |  | 120
10 |  | 400 | 10 |  | 160 | 10 |  | 120 | 10 |  | 120
11 |  |  | 11 |  | 120 | 11 |  | 120 | 11 |  | 120
12 |  |  | 12 |  | 600 | 12 |  |  | 12 |  | 600
13 |  |  | 13 |  | 600 | 13 |  |  | 13 |  | 600
14 |  |  | 14 |  | 160 | 14 |  | 400 | 14 |  | 300
15 |  |  | 15 |  | 40 | 15 |  | 120 | 15 |  | 120
16 |  | 120 | 16 |  | 160 | 16 |  | 120 | 16 |  | 120
17 |  | 120 | 17 |  | 120 | 17 |  | 120 | 17 |  | 120
18 |  | 120 | 18 |  | 600 | 18 |  |  | 18 |  | 600
19 |  | 400 | 19 |  | 600 |  |  | 2280 |  |  | 5580
20 |  |  | 20
21 |  | 150 |  |  | 5640
22 |  | 400
23 |  | 400
24
25
26
27
28
3230
| D2L1 | LOAD [VA] |  | D2L2 | LOAD [VA] |  | D2L3 | LOAD [VA] |  | C2L1 | LOAD [VA]
1 |  | 320 | 1 |  | 600 | 1 |  | 600 | 1 |  | 600
2 |  | 450 | 2 |  | 700 | 2 |  | 100 | 2 |  | 160
3 |  | 320 | 3 |  | 100 | 3 |  | 100 | 3 |  | 40
4 |  | 100 | 4 |  | 100 | 4 |  | 100 | 4 |  | 160
5 |  | 100 | 5 |  | 100 | 5 |  |  | 5
6 |  | 100 | 6 |  |  | 6 |  |  | 6 |  | 600
7 |  |  | 7 |  |  | 7 |  | 700 | 7 |  | 160
8 |  | 320 | 8 |  |  | 8 |  |  | 8 |  | 40
9 |  | 450 | 9 |  |  | 9 |  | 600 | 9 |  | 160
10 |  | 320 | 10 |  | 600 | 10 |  | 100 | 10
11 |  | 100 | 11 |  | 100 | 11 |  | 100 | 11 |  | 600
12 |  | 100 | 12 |  | 100 | 12 |  | 100 | 12 |  | 160
13 |  | 100 | 13 |  | 100 | 13 |  |  | 13 |  | 40
14 |  |  | 14 |  |  | 14 |  |  | 14 |  | 160
15 |  | 320 | 15 |  |  | 15 |  | 700 | 15
16 |  | 450 | 16 |  | 700 | 16 |  |  | 16 |  | 800
17 |  | 320 | 17 |  | 400 | 17 |  | 600 | 17 |  | 400
18 |  | 100 | 18 |  | 100 | 18 |  | 100 | 18 |  | 150
19 |  | 100 | 19 |  | 100 | 19 |  | 100 | 19 |  | 150
20 |  | 100 | 20 |  | 100 | 20 |  | 100 | 20 |  | 150
21 |  |  | 21 |  |  | 21 |  |  | 21 |  | 200
22 |  |  | 22 |  |  | 22 |  |  | 22 |  | 600
23 |  |  | 23 |  | 700 | 23 |  | 700 | 23 |  | 250
24 |  |  | 24 |  |  | 24 |  |  | 24 |  | 200
|  | 4170 |  |  | 4600 |  |  | 4800 | 25 |  | 50
[9 empty] | 26 |  | 200
27
28
6030
| C2L2 | LOAD [VA] |  | LTL | LOAD [W] |  | D2121 | LOAD [VA] |  | D2122 | LOAD [VA]
1 |  | 600 | 1 |  | 3100 | 1 |  | 520 | 1 |  | 480
2 |  | 300 | 2 |  | 100 | 2 |  | 440 | 2 |  | 480
3 |  | 200 | 3 |  | 600 | 3 |  | 100 | 3 |  | 100
4 |  | 50 | 4 |  | 600 | 4 |  | 100 | 4 |  | 100
5 |  | 200 | 5 |  | 600 | 5 |  | 100 | 5 |  | 100
6 |  |  | 6 |  | 600 | 6 |  |  | 6
7 |  | 600 | 7 |  | 600 | 7 |  |  | 7
8 |  | 300 | 8 |  | 600 | 8 |  |  | 8
9 |  | 200 | 9 |  | 600 | 9 |  | 520 | 9 |  | 480
10 |  | 50 | 10 |  | 600 | 10 |  | 440 | 10 |  | 480
11 |  | 200 | 11 |  | 600 | 11 |  | 100 | 11 |  | 100
12 |  |  | 12 |  | 1200 | 12 |  | 100 | 12 |  | 100
13 |  | 600 | 13 |  | 2200 | 13 |  | 100 | 13 |  | 100
14 |  | 300 | 14 |  | 1800 | 14 |  |  | 14
15 |  | 200 | 15 |  | 600 | 15 |  |  | 15
16 |  | 50 | 16 |  |  | 16 |  |  | 16
17 |  | 200 | 17 |  |  | 17 |  | 520 | 17 |  | 480
18 |  |  | 18 |  |  | 18 |  | 440 | 18 |  | 480
19 |  | 600 | 19 |  |  | 19 |  | 100 | 19 |  | 100
20 |  | 300 | 20 |  |  | 20 |  | 100 | 20 |  | 100
21 |  | 200 | 21 |  |  | 21 |  | 100 | 21 |  | 100
22 |  | 50 | 22 |  |  | 22 |  |  | 22
23 |  | 200 | 23 |  |  | 23 |  |  | 23
24 |  |  | 24 |  |  | 24 |  |  | 24
|  | 5400 |  |  | 14400 |  |  | 3780 |  |  | 3780
|  |  |  | LT12 | LOAD [W]
|  |  | 1 |  | 600
|  |  | 2 |  | 600
|  |  | 3 |  | 600
|  |  | 4 |  | 600
|  |  | 5 |  | 600
|  |  | 6 |  | 600
|  |  | 7 |  | 2000
|  |  | 8 |  | 2000
9
10
11
12
7600

## feeder schedule
FEEDER | PHASE | GROUND | CONDUIT | NOM. AMP RATING | PHASE | GROUND | CONDUIT | FEEDER | TAG | SIZE [kVA] | TYPE | PRIMARY |  |  | SECONDARY
№ | [7 empty] | № |  |  |  | AMPS | VOLTS | FEEDER | AMPS | VOLTS | FEEDER
1 | 3 -#4 | 1 -#10 | 1 - 1" | 60 | 4 -#4 | 1 -#10 | 1 - 1¼" | 2 | T3 | 30 | Dry | 36 | 481.1252 | 3-#4 &1-#10G, 1”C | 83 | 208.6808 | 4-#1 & 1-#8G, 1½”C
3 | 3 -#4 | 1 -#8 | 1 - 1" | 70 | 4 -#4 | 1 -#8 | 1 - 1¼" | 4 | T4 | 45 | Dry | 54 | 481.1252 | 3-#3 & 1-#8G, 1¼”C | 125 | 207.8461 | 4-#1/0 & 1-#6G, 2”C
5 | 3 -#1 | 1 -#8 | 1 - 1½" | 100 | 4 -#1 | 1 -#8 | 1 - 1½" | 6 | T5 | 75 | Dry | 90 | 481.1252 | 3-#1/0 & 1-#6G, 1½”C | 208 | 208.1792 | 4-250 kcmil & 1-#4G, 3”C
7 | 3 -#1/0 | 1 -#6 | 1 - 1½" | 125 | 4 -#1/0 | 1 -#6 | 1 - 2" | 8 | T7 | 150 | Dry | 181 | 478.4671 | 3-350 kcmil & 1-#4G, 3”C | 417 | 207.68 | 4-250 kcmil & 2-#2G, 3”C
9 | 3 -#1/0 | 1 -#6 | 1 - 1½" | 150 | 4 -#1/0 | 1 -#6 | 1 - 2" | 10
11 | 3 -#2/0 | 1 -#6 | 1 - 2" | 175 | 4 -#2/0 | 1 -#6 | 1 - 2" | 12
13 | 3 -#3/0 | 1 -#6 | 1 - 2" | 200 | 4 -#3/0 | 1 -#6 | 1 - 2" | 14
15 | 3 -#4/0 | 1 -#4 | 1 - 2" | 225 | 4 -#4/0 | 1 -#4 | 1 - 2½" | 16
17 | 3 - 250 kcmil | 1 -#4 | 1 - 2½" | 250 | 4 - 250 kcmil | 1 -#4 | 1 - 3" | 18
19 | 3 - 350 kcmil | 1 -#4 | 1 - 3" | 300 | 4 - 350 kcmil | 1 -#4 | 1 - 3" | 20
21 | 3 - 500 kcmil | 1 -#3 | 1 - 3½" | 350 | 4 - 500 kcmil | 1 -#3 | 1 - 4" | 22
23 | 3 - 600 kcmil | 1 -#3 | 1 - 3½" | 400 | 4 - 600 kcmil | 1 -#3 | 1 - 4" | 24
25 | 6 - 250 kcmil | 2 -#2 | 2 - 2½" | 500 | 8 - 250 kcmil | 2 -#2 | 2 - 3" | 26
27 | 6 - 350 kcmil | 2 -#1 | 2 - 3" | 600 | 8 - 350 kcmil | 2 -#1 | 2 - 3" | 28
29 | 6 - 600 kcmil | 2 -#1/0 | 2 - 3½" | 800 | 8 - 600 kcmil | 2 -#2/0 | 2 - 4" | 30
31 | 9 - 400 kcmil | 3 -#2/0 | 3 - 3" | 1000 | 12 - 400 kcmil | 3 -#2/0 | 3 - 3" | 32
33 | 9 - 600 kcmil | 3 -#3/0 | 3 - 3½" | 1200 | 12 - 600 kcmil | 3 -#3/0 | 3 - 3" | 34
35 | 12 - 600 kcmil | 4 -#4/0 | 4 - 3½" | 1600 | 16 - 600 kcmil | 4 -#4/0 | 4 - 4" | 36
NOTE: ALL CONDUCTOR SIZES ARE FOR COPPER CONDUCTORS. N.E.C. TABLE 310-16
HP | FEEDER - 480 V, 3Ø, 3W
½ | 3#12 & 1#12G - ¾"C
¾ | 3#12 & 1#12G - ¾"C
1 | 3#12 & 1#12G - ¾"C
1½ | 3#12 & 1#12G - ¾"C
2 | 3#12 & 1#12G - ¾"C
3 | 3#12 & 1#12G - ¾"C
5 | 3#12 & 1#12G - ¾"C
7½ | 3#10 & 1#10G - ¾"C
10 | 3#10 & 1#10G - ¾"C
15 | 3#8 & 1#10G - ¾"C
20 | 3#6 & 1#8G - ¾"C
25 | 3#6 & 1#8G - ¾"C
30 | 3#4 & 1#6G - 1"C
40 | 3#3 & 1#6G - 1¼"C
50 | 3#1 & 1#6G - 1½"C
60 | 3#1/0 & 1#6G - 1½"C
75 | 3#2/0 & 1#4G - 2"C
100 | 3#3/0 & 1#3G - 2"C
125 | 3#4/0 & 1#3G - 2"C