## Slide 1
SEAN KIM
L/E option
AE Thesis Presentation

## Slide 2
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
“The Logan family sees the center not as a building project… but as a way to improve the quality of life for students and faculty of the University, as well as the community.”
- David Logan
David Logan, and Reva Logan
[From: http://arts.uchicago.edu/logan-center/about-logan-center]
Notes: On May 3, 2007, the University of Chicago made a historic announcement: David Logan, AB'39, JD'41, and his wife Reva and their sons and grandchildren had generously committed a $35 million gift to support the University’s Center for the Creative and Performing Arts. Not only was this one of the largest single donor gifts to the University, it is also believed to be both the single largest cash gift to the arts in the city of Chicago and one of the largest gifts to support a university arts building in the United States. Five years after the Logan family gave their record gift of $35 million, the Logan Center for the Arts celebrated its grand opening.

## Slide 3
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Reva and David Logan Center for the Arts
Building Type: Multidisciplinary arts center
Size: 184,000 square foot
Stories:
11-story tower with
3-story adjacent building
Owner: University of Chicago
Design Architect: Tod Williams Billie Tsien Architects
Lighting Design: Refro Design Group
MEP Engineer:
Ambrosino Depinto &Schmieder Consulting Engineering
Construction Manager: Turner Construction, LLC
[From: http://arts.uchicago.edu/logan-center/about-logan-center]
[From: google map]
[From: http://arts.uchicago.edu/logan-center/about-logan-center]

## Slide 4
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Lighting Depth │ Main Lobby
Lighting Depth │ Performance Hall
Lighting Depth │ Performance Penthouse
Lighting Depth │ Courtyard
Electrical Depth │ Size reduction of Emergency Generator
Lighting Depth │ MCB for Main Distribution Switchboard
Lighting Depth │ High-Efficiency dry-type Transformer
Acoustical Breadth │ Reverberation Time & Bass Ratio
Acoustical Breadth for Performance Hall
Mechanical Breadth │ Solar Heat Gain & Cooling Load of Different Mechanical Mechanical Breadth │ Glazing type on the Corridor

## Slide 5
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Lighting Depth │ Main Lobby
Lighting Depth │ Performance Hall
Lighting Depth │ Performance Penthouse
Lighting Depth │ Courtyard
Electrical Depth │ Size reduction of Emergency Generator
Lighting Depth │ MCB for Main Distribution Switchboard
Lighting Depth │ High-Efficiency dry-type Transformer
Acoustical Breadth │ Reverberation Time & Bass Ratio
Acoustical Breadth for Performance Hall
Mechanical Breadth │ Solar Heat Gain & Cooling Load of Different Mechanical Mechanical Breadth │ Glazing type on the Corridor

## Slide 6
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Entry Lobby
Corridor
Powerful atmosphere
Create welcoming environment
Way finding
Public impressions
Design Goal
[From: http://facilities.uchicago.edu/construction/performing-arts/]

## Slide 7
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
- Tod Williams & Billie Tsien, Architects
“The idea of the low, sky lit building of studios and theaters, and the tower of the arts came from imagining the flat prairies of the Midwest and the great towers of Chicago.”
http://arts.uchicago.edu/logan-center/about/about-logan-center-0
[From: google map, University of Chicago, ]

## Slide 8
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
LED Cove Lighting

## Slide 9
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
LED Cove Lighting
LED Wall glazing

## Slide 10
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
LED Cove Lighting
LED Wall glazing
Compact Fluorescent Downlight

## Slide 11
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion

## Slide 12
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Eh (lux) Avg:Min
50
4:1
95.19
1.92:1
150
4:1
164.6
2.2:1
IES Criteria: Lobby
Design Proposed: Lobby
IES Criteria: Reception Desk
Design Proposed: Reception Desk
ASHRAE 90.1 (2010): Lobby
Design Proposed: Lobby
Power Density (W/ft2)
1.3
0.64

## Slide 13
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion

## Slide 14
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Eh (lux) Avg:Min
50
4:1
95.8
1.85:1
IES Criteria: Corridor
Design Proposed: Corridor
ASHRAE 90.1 (2010): Lobby
Design Proposed: Lobby
Power Density (W/ft2)
0.5
0.87

## Slide 15
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Design Goal
Uniform Light Distribution with Comfort
Pleasant Environment with Relax Atmosphere
Avoid Visual Distraction
Three Design Concepts
[From: http://facilities.uchicago.edu/construction/performing-arts/]

## Slide 16
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Modernism
Sophisticated
Classical
Dynamic with Linear
Intense glare but simple
Greek Doric Columns

## Slide 17
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Modernism
Sophisticated
Classical

## Slide 18
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Eh (lux) Avg:Min
100
2:1
112.3
1.8:1
117.8
2.2:1
95.3
2.1:1
IES Design Criteria
Modernism
Sophisticated
Classical
ASHRAE 90.1 (2010)
Modernism
Power Density (W/ft2)
2.6
0.72
Sophisticated
Classical
0.76
0.57

## Slide 19
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Egress Lighting
LED Seat Light
Wall Surface “Exit” panel
Eh
0.2 fc
0.38 fc
N.F.P.A. Code Minimum
Design Proposed

## Slide 20
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Design Goal
Uniform Light Distribution
Flexible lighting
Provide different Scenes for various activities
[From: http://facilities.uchicago.edu/construction/performing-arts/]

## Slide 21
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1
Zone 2
Zone 3
Zone 4
Zone 5
Custom LED Pendant Light
(2) for down, (1) for Up
LED Spot Light
3” aperture Recessed Downlight

## Slide 22
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – 100% Output
Zone 2 – 100% Output
Zone 3 – 100% Output
Zone 4 – ON
Zone 5 – ON
Eh (lux) Avg:Min
300
1.5:1
338.26
1.6:1
IES Criteria: Dance (Performance)
Design Proposed: All Lights On
ASHRAE 90.1 (2010)
Design Proposed: Lobby
Power Density (W/ft2)
1.4
1.1

## Slide 23
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – 100% Output
Zone 2 – 100% Output
Zone 3 – 100% Output
Zone 4 – ON
Zone 5 – ON

## Slide 24
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – 50% Output
Zone 2 – 50% Output
Zone 3 – 50% Output
Zone 4 – ON
Zone 5 – ON

## Slide 25
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – OFF
Zone 2 – OFF
Zone 3 – OFF
Zone 4 – ON
Zone 5 – ON

## Slide 26
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – OFF
Zone 2 – OFF
Zone 3 – OFF
Zone 4 – OFF
Zone 5 – OFF
December 22, 10:00 am

## Slide 27
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – OFF
Zone 2 – OFF
Zone 3 – OFF
Zone 4 – OFF
Zone 5 – OFF
December 22, 10:00 am with Shade
December 22, 10:18 am with Shade

## Slide 28
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Zone 1 – 50% Output
Zone 2 – 25% Output
Zone 3 – Only Uplight
Zone 4 – OFF
Zone 5 – ON

## Slide 29
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Study of High Efficiency transformer
with Energy cost saving

## Slide 30
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Schedule of Existing Transformers in Logan Center for the Arts |  |  |  |  |  | 
No. | Rating of Unit | Primary V | Secondary V | Location | Feeding to | Note
T-1 | 150 kVA | 277/480 | 120/208 | Lower Level | to LV-EM-LL | Switchboard
T-2 | 57 kVA | 277/480 | 120/208 | Lower Level | to EM-PP-LL | Panelboard
T-3 | 45 kVA | 277/480 | 120/208 | First Floor | to PP-TH-1 | Panelboard
T-4* | 30 kVA | 277/480 | 120/208 | Lower Level | to LP-AV-LL | Panelboard
T-5* | 30 kVA | 277/480 | 120/208 | First Floor | to LP-AV-1 | Panelboard
T-6 | 76 kVA | 277/480 | 120/208 | Eleventh Floor | to TLP-7-11 | Panelboard
T-7 | 300 kVA | 277/480 | 120/208 | Lower Level | to LV-DP-LL-N | Switchboard
T-8 | 112.5 kVA | 277/480 | 120/208 | Second Floor | to TLP-3-6 | Panelboard
T-9 | 75 kVA | 277/480 | 120/208 | Second Floor | to PNL-#1 | THEATRICAL BRK at 245
T-10 | 45 kVA | 277/480 | 120/208 | Second Floor | to PP-TH-2B | Panelboard
T-11 | 225 kVA | 277/480 | 120/208 | Lower Level | to SP-201, Dimmer Racks 201,202 | at 245
T-12 | 150 kVA | 277/480 | 120/208 | First Floor | to SP-101, Dimmer Racks 101,102 | at 245
T-13 | 75 kVA | 277/480 | 120/208 | Second Floor | to PNL-#2 | THEATRICAL BRK at 245
T-14 | 45 kVA | 277/480 | 120/208 | Second Floor | to PP-TH-2A | Panelboard
T-15 | not shown in Single-Line Diagram |  |  |  |  | 
T-16 | 45 kVA | 277/480 | 120/208 | Third Floor | to PP-SR | Panelboard
T-17 | 75 kVA | 277/480 | 120/208 | Second Floor | to PNL-#1 | THEATRICAL BRK at 210B
T-18 | 75 kVA | 277/480 | 120/208 | Second Floor | to PNL-#2 | THEATRICAL BRK at 210B
T-19 | 225 kVA | 277/480 | 120/208 | Second Floor | to Dimmer Racks 1,2,3 | at 210B
T-20 | 500 kVA | 277/480 | 120/208 | Lower Level | to LV-SB-SS-S | Switchboard
T-21 | 45 kVA | 277/480 | 120/208 | Lower Level | to Courtyard Projection | 
T-22 | 30 kVA | 277/480 | 120/208 | Eleventh Floor | to Dimmer Racks 301 | at 301
T-23 | 45 kVA | 277/480 | 120/208 | Lower Level | to LP-LL-NA | Panelboard
Total 22 K-rated transformers
NEMA TP-1 for energy efficiency
T-4 and T-5 are designed as Isolation transformer
T-20 with 500KVA is designed K-factor of 13
Rating of Unit | # of Unit
30 kVA | 3
45 kVA | 6
57 kVA | 1
75 kVA | 4
76 kVA | 1
112.5 kVA | 1
150 kVA | 2
225 kVA | 2
300 kVA | 1
500 kVA | 1
Total | 22
Existing Transformers
Proposed Solution
EATON: Premium efficient transformer
30% less losses than NEMA TP- 1 for energy consumption
Reduced operating costs
Available as K-factor or harmonic mitigating

## Slide 31
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Energy Cost Savings: $4,119 per year
Reduction in Power Lost by Transformer: 38.96 MW per year
HVAC Savings: 19.48 MBT per year
Summary
Total Loss Per Year
Energy Life Cycle Costs
Proposed Solution
EATON: Premium efficient transformer
30% less losses than NEMA TP- 1 for energy consumption
Reduced operating costs
Available as K-factor or harmonic mitigating

## Slide 32
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Study of Solar Heat Gain & Cooling Loads
with Different glazing type

## Slide 33
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Elevation View
Existing Glazing type
Dimension: 90.88’ L x 10’ H
Area: 908.8 sq.ft
East-facing window
First Floor Plan View
N
Double Glazing type
Thickness: 1 3/16”
SHGC: 0.41
U-Value (winter): 0.3 Btu/hr*Sqft*F
http://www.ppg.com/corporate/ideascapes/glass/Pages/default.aspx

## Slide 34
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Existing Glazing type
Double Glazing type
Thickness: 1 3/16”
SHGC: 0.41
U-Value (winter): 0.3 Btu/hr*Sqft*F
Proposed 1
Proposed 2
Triple Glazing type
Thickness: 1 13/16”
SHGC: 0.23
U-Value (winter): 0.12 Btu/hr*Sqft*F
Single Glazing type
Thickness: 1/2”
SHGC: 0.36
U-Value (winter): 0.95 Btu/hr*Sqft*F
http://www.ppg.com/corporate/ideascapes/glass/Pages/default.aspx
http://www.ppg.com/corporate/ideascapes/glass/Pages/default.aspx
http://www.ppg.com/corporate/ideascapes/glass/Pages/default.aspx

## Slide 35
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Total Cooling Load
Solar Heat Gain for Summer
Cooling Load for Summer
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 1894.2148 | 1653.1754 | 1420.6372 | 1233.0079 | 1100.3426 | 13412.1979 | 36727.1006 | 44702.3716 | 44316.5733 | 37610.5037 | 26584.5029 | 15846.2221 | 13272.4891 | 13078.3053 | 12975.9469 | 12345.3899 | 11192.6828 | 9581.2956 | 7411.2049 | 4456.645 | 3526.215 | 3006.5283 | 2539.9439 | 2168.4357
Proposed 1 - Triple | 757.6859 | 661.2701 | 568.2549 | 493.2032 | 440.137 | 7352.4317 | 20412.8453 | 24845.9258 | 24555.5281 | 20691.9748 | 14388.9637 | 8234.2418 | 6669.904 | 6473.3505 | 6357.5275 | 5987.1845 | 5367.2299 | 4521.3539 | 3390.707 | 1834.5964 | 1410.486 | 1202.6113 | 1015.9776 | 867.3743
Proposed 2 - Single | 5998.3469 | 5235.0553 | 4498.6845 | 3904.525 | 3484.4183 | 14214.5847 | 34951.7571 | 42535.2346 | 43248.1897 | 38804.5654 | 30796.4684 | 23227.4583 | 22681.2814 | 23756.5025 | 24496.9444 | 24179.5151 | 22787.9841 | 20547.4743 | 17409.1012 | 13374.2916 | 11166.3475 | 9520.6729 | 8043.1556 | 6866.713
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 2801.2652 | 2389.173 | 2040.5455 | 1751.4178 | 1521.9862 | 7355.6892 | 21053.8837 | 30988.1897 | 35895.6944 | 35582.5265 | 30693.9371 | 23646.9255 | 19284.0952 | 16914.4876 | 15474.8604 | 14306.219 | 13085.0338 | 11659.2927 | 9889.8887 | 7593.7181 | 5980.5401 | 4847.3743 | 3983.8846 | 3315.3015
Proposed 1 - Triple | 1182.0625 | 999.718 | 848.3103 | 724.3238 | 626.6309 | 3919.2061 | 11606.7296 | 17164.0663 | 19876.4627 | 19634.6167 | 16805.2638 | 12747.7252 | 10191.1967 | 8764.6017 | 7878.0236 | 7171.5576 | 6469.5033 | 5684.3738 | 4736.3261 | 3515.3711 | 2688.3788 | 2130.7725 | 1721.6386 | 1413.904
Proposed 2 - Single | 7995.5141 | 6939.4648 | 6005.468 | 5208.4038 | 4566.0396 | 9403.8283 | 21386.4354 | 30330.5556 | 35216.7169 | 35882.4396 | 32826.5358 | 28122.2934 | 25842.4253 | 25145.1669 | 25004.0087 | 24701.3502 | 23870.7698 | 22410.2427 | 20223.3182 | 17252.6175 | 14727.7803 | 12622.8416 | 10794.6316 | 9250.4229
Chart: 
| Existing Glazing - Double | Proposed Type 1 - Triple | Proposed Type 2 - Single
 | 322055.9 | 168500.8 | 455729.3
After Noon
Btu/Hr
Btu/Hr
Btu
133673.4 Btu More
153555.1 Btu less

## Slide 36
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Total Cooling Load
Summary
Chart: 
| Existing Glazing - Double | Proposed Type 1 - Triple | Proposed Type 2 - Single
 | 322055.9 | 168500.8 | 455729.3
Btu
153555.1 Btu less
133673.4 Btu More
(June, 21 in the Corridor) (* 0.112 $/Kwh)
Chart: 
| Exisitng -Double | Proposed Type 1 - Triple | Proposed Type 2 - Single
 | 10.56 | 5.53 | 14.84
$
10.56
5.53
14.84

## Slide 37
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Acknowledgements
Dr. Houser
Dr. Mistrick
Professor Parfitt
W. Blair Malcom
Eric Eichler
Thank you!
Conclusion
Lighting: Provided various lighting designs reflecting the purpose of the space
Electrical: Saved $4,119 per year in energy cost with High-efficiency transformer
Mechanical: Triple pane in the corridor provides 47% of cooling load cost saving during the summer.
References
- DiLaura DL, Houser KW, Mistrick RG, Steff GR. Illuminating Engineering Society The Lighting HandBook
10th Edition.
- ASHRAE Standard 90.1, 2007 – Energy Standard for Building Except Low-Rise Residential Buildings.
- National fire Protection Association 101, 2009: Life Safety Code – 7.8 Illumination of Means of Egress.
- Facilities Services Facility Standards (FS) 2 of the Univeristy of Chicago, Volume III, M-Electrical Systems.
- Kotey, Nathan A.; Wright, John L.; Collins, Michael R.; Barnaby, Charles S. "Solar gain through windows with shading devices: simulation versus measurement" The Free Library 01 July 2009. 09 April 2014 , Retrieved from http://www.thefreelibrary.com/Solar gain through windows with shading devices: simulation versus...-a0217848187.
- “Energy Savings Calculator for Eaton Transformers”, 2013, Eaton Corporation, Retrieved from <http://es.eaton.com/transformercalc/index.php#calc>
- “Glass Configuration tools”, 2014, PPG Industries, Retrieved from http://construct.ppg.com.

## Slide 38
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Total Cooling Load & Heat Gain
Solar Heat Gain for Summer
Cooling Load for Summer
June, 21 | Total Cooling Load & Heat Gain
Existing Glazing - Double | 322055.9 BTU
Proposed Type 1 - Triple | 168500.8 BTU
Proposed Type 2 - Single | 455729.3 BTU
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 1894.2148 | 1653.1754 | 1420.6372 | 1233.0079 | 1100.3426 | 13412.1979 | 36727.1006 | 44702.3716 | 44316.5733 | 37610.5037 | 26584.5029 | 15846.2221 | 13272.4891 | 13078.3053 | 12975.9469 | 12345.3899 | 11192.6828 | 9581.2956 | 7411.2049 | 4456.645 | 3526.215 | 3006.5283 | 2539.9439 | 2168.4357
Proposed 1 - Triple | 757.6859 | 661.2701 | 568.2549 | 493.2032 | 440.137 | 7352.4317 | 20412.8453 | 24845.9258 | 24555.5281 | 20691.9748 | 14388.9637 | 8234.2418 | 6669.904 | 6473.3505 | 6357.5275 | 5987.1845 | 5367.2299 | 4521.3539 | 3390.707 | 1834.5964 | 1410.486 | 1202.6113 | 1015.9776 | 867.3743
Proposed 2 - Single | 5998.3469 | 5235.0553 | 4498.6845 | 3904.525 | 3484.4183 | 14214.5847 | 34951.7571 | 42535.2346 | 43248.1897 | 38804.5654 | 30796.4684 | 23227.4583 | 22681.2814 | 23756.5025 | 24496.9444 | 24179.5151 | 22787.9841 | 20547.4743 | 17409.1012 | 13374.2916 | 11166.3475 | 9520.6729 | 8043.1556 | 6866.713
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 2801.2652 | 2389.173 | 2040.5455 | 1751.4178 | 1521.9862 | 7355.6892 | 21053.8837 | 30988.1897 | 35895.6944 | 35582.5265 | 30693.9371 | 23646.9255 | 19284.0952 | 16914.4876 | 15474.8604 | 14306.219 | 13085.0338 | 11659.2927 | 9889.8887 | 7593.7181 | 5980.5401 | 4847.3743 | 3983.8846 | 3315.3015
Proposed 1 - Triple | 1182.0625 | 999.718 | 848.3103 | 724.3238 | 626.6309 | 3919.2061 | 11606.7296 | 17164.0663 | 19876.4627 | 19634.6167 | 16805.2638 | 12747.7252 | 10191.1967 | 8764.6017 | 7878.0236 | 7171.5576 | 6469.5033 | 5684.3738 | 4736.3261 | 3515.3711 | 2688.3788 | 2130.7725 | 1721.6386 | 1413.904
Proposed 2 - Single | 7995.5141 | 6939.4648 | 6005.468 | 5208.4038 | 4566.0396 | 9403.8283 | 21386.4354 | 30330.5556 | 35216.7169 | 35882.4396 | 32826.5358 | 28122.2934 | 25842.4253 | 25145.1669 | 25004.0087 | 24701.3502 | 23870.7698 | 22410.2427 | 20223.3182 | 17252.6175 | 14727.7803 | 12622.8416 | 10794.6316 | 9250.4229

## Slide 39
Introduction
Building Overview
Lighting Depth │ Main Lobby
Electrical Depth
Performance Hall
Performance Penthouse
Mechanical Breadth
Conclusion
Total Cooling Load & Heat Gain
Solar Heat Gain for Winter
Cooling Load for winter
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 1639.2867 | 1408.0174 | 1223.8972 | 1094.6349 | 1068.0931 | 1191.995 | 1455.6761 | 17038.934 | 28151.1029 | 22090.6601 | 12462.1103 | 9580.8741 | 9485.0309 | 9184.4957 | 8105.6705 | 5839.6018 | 5275.1343 | 4728.1923 | 4096.7971 | 3493.6098 | 2978.0167 | 2514.985 | 2150.4097 | 1879.7437
Proposed 1 - Triple | 655.7147 | 563.2069 | 489.5589 | 437.8539 | 427.2372 | 476.798 | 582.2704 | 9248.0973 | 15379.0359 | 11860.6724 | 6328.1814 | 4592.9531 | 4453.414 | 4228.3075 | 3609.3378 | 2366.8281 | 2110.0537 | 1891.2769 | 1638.7188 | 1397.4439 | 1191.2067 | 1005.994 | 860.1639 | 751.8975
Proposed 2 - Single | 5191.0745 | 4458.7217 | 3875.6744 | 3466.3438 | 3382.2947 | 3774.6509 | 4609.641 | 19373.017 | 30590.3898 | 26955.2245 | 20364.892 | 19525.8047 | 20661.1052 | 21200.6843 | 20449.2655 | 18051.519 | 16704.5919 | 14972.609 | 12973.1907 | 11063.0976 | 9430.3861 | 7964.1192 | 6809.6308 | 5952.5218
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Existing glazing - Double | 2179.4365 | 1886.3205 | 1636.7976 | 1436.2763 | 1309.4746 | 1290.1945 | 1390.2505 | 8982.1775 | 17516.4792 | 18596.4655 | 15047.9814 | 12474.5728 | 11257.2745 | 10433.87 | 9462.6644 | 7893.6834 | 6838.3018 | 6002.2081 | 5244.3166 | 4548.3473 | 3928.4809 | 3373.1794 | 2898.605 | 2509.6104
Proposed 1 - Triple | 884.7539 | 764.2127 | 662.0326 | 580.0944 | 528.0953 | 519.4269 | 558.7259 | 4775.43 | 9495.4737 | 10013.214 | 7917.5087 | 6365.1188 | 5585.8819 | 5046.2913 | 4452.536 | 3557.2787 | 2981.7334 | 2558.8226 | 2201.7958 | 1889.56 | 1619.7834 | 1383.2576 | 1183.7254 | 1021.4701
Proposed 2 - Single | 6717.0206 | 5835.6627 | 5079.2141 | 4468.8221 | 4085.4584 | 4038.0007 | 4365.1299 | 11630.9185 | 20083.9882 | 22284.8822 | 20663.2541 | 19950.0846 | 20251.2355 | 20632.6463 | 20475.5652 | 19312.5638 | 18151.3306 | 16761.5417 | 15127.4337 | 13404.7549 | 11752.2063 | 10198.5528 | 8833.6748 | 7696.5088
December, 21 | Total Cooling Load & Heat Gain
Existing Glazing - Double | 158137 BTU
Proposed Type 1 - Triple | 102726.3 BTU
Proposed Type 2 - Single | 311800.5 BTU