## Slide 1
Matthew Neal
Mechanical Option
Dr. Stephen Treado, Adviser

## Slide 2: Overview The Gaige Technology and Business Innovation Building
Reading, PA – PSU Berks Campus
Classrooms, Labs and Offices
~ 64,000 SF
Constructed in 2010/2011
$25.7 Million
LEED Gold
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 3: Existing Conditions Mechanical Design
Packaged Roof-Top Units
  VAV with Reheat
  CO2 and Occupancy Sensors
Fin tube / Radiant Panel Heating
Natural Gas & Electricity Utilities
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 4: Existing Conditions Energy Model
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: 
| 41395 | 41365 | 41334 | 41306 | 41275 | 41244 | 41214 | 41183 | 41153 | 41122 | 41091 | 41061 | 41030
Natural Gas | 907.14 | 1183.46 | 2362.56 | 2943.24 | 2981.32 | 2038.23 | 2162.73 | 973.28 | 556.66 | 477.28 | 447.51 | 397.9 | 576.5
Electricity | 4265.67 | 4710.63 | 3570.67 | 3009.92 | 3100.61 | 3208.13 | 2910.63 | 2566.9 | 7505.12 | 6554.93 | 6814.2 | 5172.78 | 3752.18
Initially modeled using Trace 700
  Based on engineer’s model

## Slide 5: Existing Conditions Energy Model
Initially modeled using Trace 700
  Based on engineer’s model
Compared to Utility Data
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Monthly Electrical Load ( kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Acutal Costs | 37800 | 45600 | 43200 | 47400 | 54000 | 55200 | 63000 | 60600 | 66600 | 60000 | 46800 | 44400
Modeled Costs | 71975 | 65439 | 76295 | 71727 | 65024 | 73716 | 82058 | 78127 | 102526 | 80010 | 71517 | 70136
Chart: Monthly Natural Gas ( MCF)
| January | February | March | April | May | June | July | August | September | October | November | December
Acutal Costs | 311 | 307 | 246 | 122 | 93 | 38 | 43 | 46 | 54 | 96 | 216 | 200
Modeled Costs | 304.1992 | 282.0686 | 253.0464 | 185.1985 | 109.8767 | 107.6442 | 102.3057 | 112.4003 | 104.9264 | 184.422 | 212.8618 | 282.0686

## Slide 6: Existing Conditions Energy Model
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Monthly Electrical Load ( kWh)
| January | February | March | April | May | June | July | August | September | October | November | December
Actual Consumption | 37800 | 45600 | 43200 | 47400 | 54000 | 55200 | 63000 | 60600 | 66600 | 60000 | 46800 | 44400
Validated Model | 44710 | 40638 | 46653 | 43729 | 49241 | 57139 | 65408 | 60434 | 63401 | 48641 | 43987 | 44041
Chart: Monthly Natural Gas Load ( MCF)
| January | February | March | April | May | June | July | August | September | October | November | December
Acutal Costs | 311 | 307 | 246 | 122 | 93 | 38 | 43 | 46 | 54 | 96 | 216 | 200
Validated Model | 306.917 | 284.3981 | 254.6965 | 124.3392 | 46.3967 | 44.0671 | 41.2523 | 46.2996 | 43.5818 | 121.3302 | 214.1236 | 284.6893
Actual Consumption
Initially modeled using Trace 700
  Based on engineer’s model
Compared to utility data
Validated to utility data
  2.1 % maximum error

## Slide 7: Geothermal Depth Initial Motivation
The Gaige Building
Large open space
Potential energy savings
Potential emissions reductions
Life-costs of system
Open area surrounding Gaige Building
Chart: Energy Consumption (Btu/hr)
| January | February | March | April | May | June | July | August | September | October | November | December
Heating | 205666.6723 | 189106.0642 | 147418.8043 | 86968.4376 | 4640.8224 | 2156.5877 | 1211.6903 | 774.1633 | 3244.3547 | 81942.9723 | 114490.6056 | 179746.2703
Cooling | 1997.7846 | 1794.0822 | 4948.5686 | 6322.2801 | 45953.4804 | 72817.9673 | 103287.6791 | 130737 | 79071.323 | 15720.2271 | 3186.5602 | 2001.8791
Lighting | 51665.677 | 46735.8749 | 56004.1621 | 49299.3856 | 19028.9405 | 18831.7211 | 17854.8369 | 56004.1621 | 49299.3856 | 53835.0902 | 51468.7988 | 49496.605
Fans | 19493.3273 | 18460.4846 | 22278.2833 | 20433.3609 | 12814.824 | 17100.4216 | 16085.3218 | 25688.3361 | 20472.2588 | 20517.6397 | 19183.5086 | 19258.5748
Pumps | 3381.0499 | 3053.8295 | 3381.0499 | 3271.8627 | 1726.8638 | 1163.5261 | 695.386 | 304.3593 | 1058.7746 | 3340.1047 | 3271.8627 | 3381.0499
Equip/Recep | 168184.7975 | 152289.8708 | 157810.9898 | 147621.0944 | 107613.5395 | 104959.2669 | 106353.1097 | 146069.9537 | 147621.0944 | 155170.7069 | 164646.791 | 166308.8249
Misc Fuel | 21135.252 | 21135.252 | 21135.252 | 26424.102 | 21135.252 | 21135.252 | 26424.102 | 21135.252 | 26424.102 | 21135.252 | 21135.252 | 26424.102
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 8: Geothermal Depth Alternative 1: Vertical Loop System
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
23,636 feet of well required
100 required vertical wells
  20% safety
  300’ well depth
  Costs per well - $3,714.25
Required Number of Vertical Bores |  |  | 
Well Depth | Required Bore Length | # of Wells | # of Wells, 20% Saftey
100 | 23636.4 | 237 | 284
200 | 23636.4 | 119 | 142
300 | 23636.4 | 79 | 95
400 | 23636.4 | 60 | 71
300 feet
6 in.
To next bore
To previous
bore
1 inch HDPE
piping
Bentonite
backfill

## Slide 9: Geothermal Depth Alternative 2: Horizontal Loop System
28,550 ft. of horizontal loops
  Based on 20% safety
  Cost per 300’: $3,435.62
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Required Number of Horizontal Loops |  | 
Loop Length | Number of Loops | Total Length
800 | 20 | 16000
775 | 1 | 775
750 | 4 | 3000
700 | 5 | 3500
675 | 1 | 675
650 | 4 | 2600
400 | 5 | 2000
 | Total Length | 28550

## Slide 10: Geothermal Depth Alternative Cost Comparisons
Increased first costs:
  Savings from original design
  Added geothermal costs
  Time & Location adjustments
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Vertical - Increased First-Costs | 
Cost Item | Amount
Increased First Cost - General | $ 655,736.06
Location Multiplier - Reading PA | 0.988
Increased First Cost - Reading | $ 647,867.23
Savings from Original Design - 2009 | $ 484,710.00
Time Multiplier - 2014 to 2009 | 0.889
Savings from Original Design - 2014 | $ 545,230.60
Overall First Cost Increase: | $ 102,636.63
Horizontal - Increased First-Costs | 
Cost Item | Amount
Increased First Cost - General | $ 601,959.52
Location Multiplier - Reading PA | 0.988
Increased First Cost - Reading | $ 594,736.01
Savings from Original Design - 2009 | $ 484,710.00
Time Multiplier - 2014 to 2009 | 0.889
Savings from Original Design - 2014 | $ 545,230.60
Overall First Cost Increase: | $ 49,505.41

## Slide 11: Geothermal Depth Annual Emissions Reductions
Little change in emissions
  Decreased natural gas emissions
  Increased electricity emissions
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Difference in Total Annual Emissions |  |  | 
Pollutant | Original Emissions (lb/yr) | Geothermal Emissions (lb/yr) | Decrease %
CO2e | 2321124.8 | 2270409.1 | 2.18%
CO2 | 2194071.2 | 2140470.1 | 2.44%
CH4 | 4526.3 | 4661.8 | -2.99%
NOx | 3896.3 | 3905.4 | -0.23%
SOx | 10799.6 | 11128.1 | -3.04%
CO | 1173.6 | 1117.3 | 4.80%
Solid Waste | 258316.8 | 266191.0 | -3.05%
Chart: Pounds of Pollutant per Year
| CO2e | CO2 | CH4 | N2O | NOx | SOx | CO | TNMOC | Lead | Mercury | PM10 | Solid Waste
Electricity | 2259377.5714 | 2129528.2857 | 4661.5894 | 50.2517 | 3895.4786 | 11128.0838 | 1108.9129 | 94.2706 | 0.18049 | 0.043629 | 120.2404 | 266191.0357
Natural Gas | 11031.5402 | 10941.8529 | 0.22422 | 0.22422 | 9.9553 | 0.056682 | 8.3678 | 0.54978 | 4.4844e-05 | 2.3319e-05 | 0.75337 | 0

## Slide 12: Geothermal Depth Annual Energy Savings
Almost eliminated natural gas consumption
Similar annual electricity consumption
  Heat pump operation
Annual Energy Savings: $8,494.00
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Monthly Costs ( $)
| January | February | March | April | May | June | July | August | September | October | November | December
Original Design | 4188 | 3854 | 3728 | 2975 | 2281 | 2829 | 3499 | 3027 | 3247 | 3185 | 3229 | 3913
Geothermal Design | 3322 | 3021 | 2674 | 2024 | 1910 | 2325 | 2715 | 2489 | 2944 | 2584 | 2530 | 2923

## Slide 13: Geothermal Depth Life Cycle Cost Analysis
Vertical Well Design:
  Simple: 12.1 years
  Discounted: 12.7 years
Horizontal Loop Design:
  Simple: 5.8 years
  Discounted: 6.1 years
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Years
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
 | -102636.63 | -92207.1049 | -82135.4661 | -72407.4002 | -63009.4852 | -53928.9039 | -45153.4135 | -36671.3165 | -28471.4336 | -20543.0777 | -12876.0294 | -5460.5142 | 1712.8199 | 8652.9226 | 15368.3615 | 21867.34 | 28157.7155 | 34247.0159 | 40142.455 | 45850.9481 | 51379.1255
Chart: Years
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
 | -49505.41 | -39075.8849 | -29004.2461 | -19276.1802 | -9878.2652 | -797.6839 | 7977.8065 | 16459.9035 | 24659.7864 | 32588.1423 | 40255.1906 | 47670.7058 | 54844.0399 | 61784.1426 | 68499.5815 | 74998.56 | 81288.9355 | 87378.2359 | 93273.675 | 98982.1681 | 104510.3455

## Slide 14: Geothermal Depth Alternative Selection
Horizontal Design
  Best Payback – 6.1 years
  Large space requirements
Vertical Design
  Favorable Payback – 12.7 years
  Less space requirements
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 15: Acoustics Breadth Onsite Measurements
Comparisons to ANSI S12.60
Reverberation Time (T30)
  0.7 for > 10,000 ft3
  0.6 for < 10,000 ft3
Chart: 
| 125 | 250 | 500 | 1000 | 2000 | 4000
Classroom 121 | 0.985 | 0.71833 | 0.49333 | 0.71 | 0.75667 | 0.63333
Classroom 246 | 0.85167 | 0.90667 | 0.59667 | 0.61833 | 0.67667 | 0.67
Classroom 247 | 0.84667 | 0.77833 | 0.58667 | 0.57333 | 0.62833 | 0.62167
Target RT | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Chart: 
| 125 | 250 | 500 | 1000 | 2000 | 4000
Classroom 120 | 0.845 | 0.74667 | 0.58667 | 0.485 | 0.49333 | 0.48167
Classroom 122 | 0.72833 | 0.73 | 0.475 | 0.55 | 0.56833 | 0.53
Classroom 248 | 0.78333 | 0.825 | 0.54333 | 0.565 | 0.56167 | 0.58667
Target RT | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
  Classrooms > 10,000 ft3
  Classrooms < 10,000 ft3
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 16: Acoustics Breadth Onsite Measurements
Comparisons to ANSI S12.60
Background Noise Level (BNL)
  NC – 30
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Octave Band Center Frequency (Hz)
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC 15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC 20 | 51 | 40 | 33 | 26 | 22 | 19 | 17 | 16
NC 25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC 30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC 35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC 40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
NC 45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC 50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC 55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC 60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC 65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
NC 70 | 83 | 79 | 75 | 73 | 71 | 69 | 68 | 67

## Slide 17: Acoustics Breadth Onsite Measurements
Comparisons to ANSI S12.60
Transmission Loss (TL) & Sound Trans. Coefficient (STC)
  STC – 50 between classrooms
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Third Octave Band Center Frequency (Hz)
| 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
TL Data | 29.5227 | 34.2067 | 38.0354 | 39.5556 | 44.2171 | 43.2935 | 44.4498 | 45.7998 | 52.2484 | 53.7319 | 52.9349 | 55.0575 | 52.3194 | 52.5779 | 55.0965 | 55.8989
Contour | 33 | 36 | 39 | 42 | 45 | 48 | 49 | 50 | 51 | 52 | 53 | 53 | 53 | 53 | 53 | 53
  Classroom 121 to 122, 49 ASTC
  Classroom 120 to 121, 46 ASTC
Chart: Third Octave Band Center Frequency (Hz)
| 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
TL Data | 25.9526 | 28.2515 | 32.3102 | 33.4555 | 38.9669 | 41.2734 | 45.6796 | 53.3046 | 51.0033 | 51.9968 | 53.9498 | 54.7874 | 52.9743 | 52.0678 | 55.0214 | 55.7938
Contour | 30 | 33 | 36 | 39 | 42 | 45 | 46 | 47 | 48 | 49 | 50 | 50 | 50 | 50 | 50 | 50

## Slide 18: Acoustics Breadth Onsite Measurements
  Classroom 246 to 247, 40 ASTC
Chart: Third Octave Band Center Frequency (Hz)
| 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
TL Data | 23.7621 | 26.4897 | 34.6675 | 38.2919 | 37.2175 | 40.8219 | 42.3 | 38.1917 | 46.0671 | 48.4381 | 46.0145 | 43.6545 | 43.1216 | 36.495 | 43.6632 | 45.4708
Contour | 24 | 27 | 30 | 33 | 36 | 39 | 40 | 41 | 42 | 43 | 44 | 44 | 44 | 44 | 44 | 44
Comparisons to ANSI S12.60
Transmission Loss (TL) & Sound Trans. Coefficient (STC)
  STC – 50 between classrooms
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
  Classroom 247 to 248, 38 ASTC
Chart: Third Octave Band Center Frequency (Hz)
| 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
TL Data | 17.7641 | 24.6777 | 27.4052 | 33.4004 | 35.8562 | 38.9449 | 39.9044 | 40.6392 | 42.1366 | 44.5794 | 44.1868 | 42.8922 | 38.7392 | 34.7822 | 38.1562 | 41.2285
Contour | 22 | 25 | 28 | 31 | 34 | 37 | 38 | 39 | 40 | 41 | 42 | 42 | 42 | 42 | 42 | 42

## Slide 19: Acoustics Breadth Onsite Measurements
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
  Classroom 247 to 248, 38 ASTC
Chart: Third Octave Band Center Frequency (Hz)
| 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000
TL Data | 17.7641 | 24.6777 | 27.4052 | 33.4004 | 35.8562 | 38.9449 | 39.9044 | 40.6392 | 42.1366 | 44.5794 | 44.1868 | 42.8922 | 38.7392 | 34.7822 | 38.1562 | 41.2285
Contour | 22 | 25 | 28 | 31 | 34 | 37 | 38 | 39 | 40 | 41 | 42 | 42 | 42 | 42 | 42 | 42

## Slide 20: Acoustics Breadth Heat Pump Sound Isolation
Option 1: ceiling plenum
Classroom & heat pump modeled in Odeon
  Inadequate background noise level
  ~ 50 to 55 dBA
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Option 2: mechanical room
  Meets 35 dBA criteria
  ~ 20 to26 dBA

## Slide 21: Acoustics Breadth Heat Pump Ductwork Noise Control
Private Offices & Classrooms
  Specify minimum lengths of duct lining
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Minimum Duct Lining Lengths |  | 
Path | Private Office | Classroom
Supply | 2 feet | 3 feet
Return | 3 feet | 5 feet
Chart: Octave Band Center Frequency (Hz)
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC 15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC 20 | 51 | 40 | 33 | 26 | 22 | 19 | 17 | 16
NC 25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC 30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC 35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC 40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
NC 45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC 50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC 55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC 60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC 65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
NC 70 | 83 | 79 | 75 | 73 | 71 | 69 | 68 | 67
  Classrooms
Chart: Octave Band Center Frequency (Hz)
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC 15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC 20 | 51 | 40 | 33 | 26 | 22 | 19 | 17 | 16
NC 25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC 30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC 35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC 40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
NC 45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC 50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC 55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC 60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC 65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
NC 70 | 83 | 79 | 75 | 73 | 71 | 69 | 68 | 67
  Offices

## Slide 22: Campus Geothermal Initial Motivation
Close proximity
All same owner
More space with vertical wells
Potential diversity benefits
Utility usage data known
  Need to know: heating, cooling, and ventilation loads
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 23: Campus Geothermal Model Validation
2003 EIA building energy use survey used
End use energy percentages estimated
Trace model created for each building
Validated to utility and EIA percentage estimates
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Model Validation Performance |  |  |  |  |  | 
Building Name | EIA Targets |  | Model Results |  | Percentage Deviations | 
 | Electricity (kWh) | Nat. Gas (therms) | Electricity (kWh) | Nat. Gas (therms) | Electricity (kWh) | Nat. Gas (therms)
The Franco Building | 163007 | 7525 | 164693 | 7905 | 1.03% | 5.04%
The Gaige Building | 223701 | 11643 | 226577 | 11816 | 1.29% | 1.49%
Thun Library | 330557 | 7041 | 331394 | 7089 | 0.25% | 0.69%
Luerssen Building | 800746 | 0 | 800627 | 0 | 0.01% | n/a
Janssen Conference Center | 101072 | 0 | 100504 | 0 | 0.56% | n/a
Perkins Student Center | 593073 | 0 | 592461 | 0 | 0.10% | n/a
Beaver Community Center | 176622 | 5607 | 177305 | 5338 | 0.39% | 4.79%
Hintz Bookstore | 31168 | 0 | 31800 | 0 | 2.03% | n/a
All Campus Residences | 455342 | 0 | 458615 | 0 | 0.72% | n/a

## Slide 24: Campus Geothermal Sizing and Layout
463,653 feet of wells required
500’ well depth used
1020 wells minimum
  1050 wells chosen
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
500 feet
6 in.
To next bore
To previous
bore
1 inch HDPE
piping
Bentonite
backfill

## Slide 25: Campus Geothermal Annual Energy Savings
Baseline and geothermal models created
  Annual Energy Savings: $58,166.00
~ 27.2 % reduction in emissions
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Chart: Monthly Natural Gas Costs ( $)
| January | February | March | April | May | June | July | August | September | October | November | December
Current Design | 25426 | 24374 | 13139 | 5903 | 14877 | 22918 | 33168 | 25348 | 14808 | 7916 | 10341 | 21572
Geothermal Redesign | 20673 | 19247 | 14406 | 7194 | 8840 | 12966 | 17933 | 15640 | 10694 | 6696 | 9586 | 17747
Difference in Total Annual Emissions |  |  | 
Pollutant | Original Design Total Emissions (lb/yr) | Geothermal Design Total Emissions (lb/yr) | Percent Decrease %
CO2e | 15258985.5 | 11108037.4 | 27.20%
CO2 | 14405155.4 | 10489303.8 | 27.18%
CH4 | 30525.2 | 22104.3 | 27.59%
N2O | 338.5 | 246.3 | 27.24%
NOx | 25923.5 | 18824.4 | 27.38%
SOx | 72849.1 | 52749.9 | 27.59%
CO | 7614.6 | 5558.6 | 27.00%
PM10 | 819.1 | 597.2 | 27.10%
Solid Waste | 1742541.0 | 1261763.3 | 27.59%

## Slide 26: Campus Geothermal Life Cycle Cost Analysis
Increased first costs estimated
  $6,358,220.94 increase
No reasonable payback period was found
  Very high increased first costs
  No savings realized from other buildings
Relatively small amount of diversity
  ~ 89.4% overall
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Building | Required Bores
The Gaige Building | 48
The Franco Building | 109
The Thun Library | 173
The Hintz Bookstore | 4
The Beaver Community Commons | 122
The Perkins Student Center | 202
The Janneson Conference Center | 37
The Luerssen Building | 284
All Campus Residences | 58
Total Bores for Campus, separate | 1038
Total Bores for Campus, together | 928
Diversity Realized | 89.4%
Campus - Increased First-Costs | 
Cost Item | Amount
Increased First Cost - Building Costs | $ 1,252,778.74
Increased First Cost – Well Field Costs | $ 5,734,520.38
Location Multiplier - Reading PA | 0.988
Increased First Cost - Reading | $ 6,903,451.53
Savings from Original Design - 2009 | $ 484,710.00
Time Multiplier - 2014 to 2009 | 0.889
Savings from Original Design - 2014 | $ 545,230.60
Overall First Cost Increase: | $ 6,358,220.94

## Slide 27: Campus Geothermal Life Cycle Cost Analysis
Effect of increased diversity
  Poor payback period with high diversity
  Not justifiable
Effect of increased initial savings
  Feasible payback with $4.5 million initial savings
  Savings from new buildings
  Savings from renovation alternatives for buildings
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions
Simple Payback with 10% Safety Factor |  |  | 
Load Diversity | Bores: 10% Safety | First Cost Increase | Simple Payback
100% | 1142 | $ 6,185,478.68 | 82.64
95% | 1085 | $ 5,906,080.61 | 78.90
90% | 1028 | $ 5,626,682.53 | 75.17
85% | 971 | $ 5,347,284.45 | 71.44
80% | 914 | $ 5,067,886.37 | 67.70
75% | 857 | $ 4,788,488.30 | 63.97
70% | 800 | $ 4,509,090.22 | 60.24
65% | 743 | $ 4,229,692.14 | 56.51
60% | 686 | $ 3,950,294.06 | 52.77
55% | 628 | $ 3,665,994.26 | 48.98
50% | 571 | $ 3,386,596.19 | 45.24
Actual Building | 1050 | $ 5,734,520.38 | 76.61
Savings Comparison – With Current Safety Factor |  |  | 
Increased Savings ($) | New First Cost | Simple Payback | Discounted Payback
Current Design | $ 5,734,520.38 | 76.61 | > 40 years
$ 1,000,000.00 | $ 4,734,520.38 | 63.25 | > 40 years
$ 3,000,000.00 | $ 2,734,520.38 | 36.53 | > 40 years
$ 4,000,000.00 | $ 1,734,520.38 | 23.17 | > 40 years
$ 4,400,000.00 | $ 1,334,520.38 | 17.83 | 30.11
$ 4,500,000.00 | $ 1,234,520.38 | 16.49 | 25.02
$ 4,600,000.00 | $ 1,134,520.38 | 15.16 | 21.56
$ 4,800,000.00 | $ 934,520.38 | 12.48 | 16.34
$ 5,000,000.00 | $ 734,520.38 | 9.81 | 12.21
$ 5,200,000.00 | $ 534,520.38 | 7.14 | 8.68
$ 5,500,000.00 | $ 234,520.38 | 3.13 | 4.10

## Slide 28: Final Conclusions Gaige Building and Campus Geothermal
Both vertical and horizontal designs feasible
  Horizontal system cheaper – 6.1 years
  Vertical system less space constraints – 12.7 years
Heat pump noise control
  Isolated through partition design
  Isolated from minimum duct lining lengths
Gaige Building compared with ANSI S12.60
  Meets requirements for RT and BNL
  Some partitions do not meet STC requirements
Campus-wide geothermal
  Not reasonable payback
  Less diversity found in campus load
  Initial savings are needed
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 29: Final Conclusions Acknowledgements
Special thanks to:
  Scott Mack & Justin Kalanesh, H. F. Lenz
  Kim Berry, Penn State Berks
  Dr. Stephen Treado, adviser
  Dr. Richard Mistrick, honors adviser
  Moses Ling
  Dr. Michelle Vigeant
  Aaron King and Cory Clippinger
  Photos courtesy of Penn State Berks and Illumination Arts
Overview
Existing Conditions
Geothermal Depth
System Alternatives
Energy & Emissions
Life Cycle Cost Analysis
Acoustics
Onsite Measurements
Heat Pumps
Campus-wide Geothermal
Conclusions

## Slide 30
Matthew Neal
Mechanical Option
Dr. Stephen Treado, Adviser
Thank You!

## Slide 31: Appendix Slides Existing Conditions
Chart: 
| Heating | Cooling | Air System Fans | Pumps | Lights | Electrical Equipment/ Receptacles | Misc. Fuel
 | 0.2388 | 0.10934 | 0.053823 | 0.006581 | 0.12198 | 0.40546 | 0.064019
Chart: Pounds of Pollutant per Year
| CO2e | CO2 | CH4 | N2O | NOx | SOx | CO | TNMOC | Lead | Mercury | PM10 | Solid Waste
Electricity | 3778422.4286 | 3561271.7143 | 7795.7106 | 84.0373 | 6514.5214 | 18609.8162 | 1854.4671 | 157.6514 | 0.30184 | 0.072963 | 201.0816 | 445158.9643
Natural Gas | 222887.2562 | 221075.1647 | 4.5302 | 4.5302 | 201.1422 | 1.1452 | 169.0681 | 11.1081 | 0.00090605 | 0.00047114 | 15.2216 | 0
Chart: 
| Electricity | Natural Gas
Site Energy Comparison | 0.52641 | 0.47359
Chart: 
| Electricity | Natural Gas
Source Energy Comparison | 0.79879 | 0.20121

## Slide 32: Appendix Slides Gaige Geothermal
Geothermal Design |  | 
Parameter | Heating | Cooling
Short-Circuit Factor (Fsc) | 1.04 | 1.04
Part-Load Factor (PLFm) | 1 | 1
Average Heat Transfer to Ground (qa) | 387000 | 387000
Block Loads (qlc and qlh) | 679400 | 1066400
Resistance of Ground, Annual pulse (Rga) | 0.215 | 0.215
Resistance of Ground, Daily pulse (Rgd) | 0.129 | 0.129
Resistance of Ground, Monthly pulse (Rgm) | 0.207 | 0.207
Resistance of Bore (Rb) | 0.09 | 0.09
Undisturbed Ground Temperature (tg) | 53 | 53
Temperature Penalty for Bore Spacing (tp) | 1.8 | 1.8
Heat Pump Inlet Temperature (twi) | 38 | 78
Heat Pump Outlet Temperature (two) | 33 | 85
System Power Input (Wc and Wh) | 3728.5 | 3728.5
Required Bore Length (Lc and Lh) | 23636.4 | 17760.4

## Slide 33: Appendix Slides Gaige Geothermal

## Slide 34: Appendix Slides Gaige Geothermal
Building Pump
Vertical Pump
Horizontal Pump

## Slide 35: Appendix Slides Gaige Geothermal
Life Cycle Rate Assumptions | 
Discount Rate | 8.00%
Escalation Rates | 
Electricity | 3.75%
Natural Gas | 5.00%
Materials | 1.73%
Main. & Labor | 1.73%
Study Period | 20 years
Vertical Geothermal Additional First Costs-Cost Per Pile |  |  |  |  |  |  |  | 
Item |  | Unit Cost |  |  |  | Amount | Units | Expense
 |  | Materials | Labor | Equipment | Total |  |  | 
Pile Boring and Filling |  | $ 1.09 | $ 5.28 | $ 3.92 | $ 10.29 | 300 | VLF | $ 3,088.41
1" HDP Pipe |  | $ 0.79 | $ - | $ - | $ 0.79 | 600 | LF | $ 474.00
1" HDP Elbow |  | $ 5.60 | $ - | $ - | $ 5.60 | 4 | Each | $ 22.40
1" HDP Joints |  | $ - | $ 5.55 | $ - | $ 5.55 | 10 | Each | $ 55.50
1" HDP Tee |  | $ 7.30 | $ - | $ - | $ 7.30 | 2 | Each | $ 14.60
Welding Machine |  | $ - | $ - | $ 40.50 | $ 40.50 | 1.47 | Each | $ 59.34
 |  |  |  |  |  |  | Total | $ 3,714.25
Chart: Diameter of Bore (inches)
| 72 | 60 | 48 | 36 | 30 | 24 | 18
Total | 186 | 140 | 102.4 | 68.5 | 52.45 | 38.05 | 30.5
Chart: 
| Pile Boring and Filling | Piping
 | 0.8315 | 0.1685

## Slide 36: Appendix Slides Gaige Geothermal
Horizontal Geothermal Additional First Costs-Cost Per Pile |  |  |  |  |  |  |  | 
Item |  | Unit Cost |  |  |  | Amount | Units | Expense
 |  | Materials | Labor | Equipment | Total |  |  | 
Trenching for piles |  | $ - | $ 0.59 | $ 0.75 | $ 1.34 | 800 | LF | $ 1,073.24
Fill for Trenches |  | $ 4.85 | $ 1.09 | $ 0.41 | $ 6.35 | 800 | LF | $ 5,079.17
Backfill for Trenches |  | $ - | $ 0.61 | $ 0.21 | $ 0.82 | 800 | LF | $ 655.64
Hauling Dirt |  | $ - | $ 0.27 | $ 0.37 | $ 0.63 | 800 | LF | $ 507.37
1" HDP Pipe |  | $ 0.79 | $ - | $ - | $ 0.79 | 1600 | LF | $ 1,264.00
1" HDP Elbow |  | $ 5.60 | $ - | $ - | $ 5.60 | 2 | Each | $ 11.20
1" HDP Joints |  | $ - | $ 5.55 | $ - | $ 5.55 | 49 | Each | $ 271.95
1" HDP Tee |  | $ 7.30 | $ - | $ - | $ 7.30 | 2 | Each | $ 14.60
Welding Machine |  | $ - | $ - | $ 40.50 | $ 40.50 | 1.47 | Days | $ 59.34
 |  |  |  |  |  |  | Total | $ 8,936.51
Chart: 
| Trenching, Filling, Removal | Piping
 | 0.8186 | 0.1814

## Slide 37: Appendix Slides Campus Geothermal
Energy Multipliers for Electric - Natural Gas Energy Source Buildings |  |  |  |  | 
Building Type | Heating |  | Cooling |  | Ventilation
 | Electricity | Nat. Gas | Electricity | Nat. Gas | 
Office - Mid Atlantic | 5.88% | 54.94% | 9.52% | 4.01% | 9.83%
Classroom - Mid Atlantic | 4.93% | 68.61% | 11.20% | 0.00% | 30.28%
Public Assembly - Mid Atlantic | 1.63% | 54.90% | 4.96% | 38.78% | 51.11%
Classroom / Office Averaged | 5.40% | 61.77% | 10.36% | 2.00% | 20.05%
Public Assembly/Classroom/Office | 4.15% | 59.48% | 8.56% | 14.26% | 30.40%
Public Assembly/Office | 3.75% | 54.92% | 7.24% | 21.39% | 30.47%
Energy Multipliers for Electric only Buildings |  |  | 
Building Type | Heating | Cooling | Ventilation
Office - Mid Atlantic | 27.99% | 7.21% | 6.18%
Public Assembly - Mid Atlantic | 39.95% | 19.08% | 20.98%
Classroom - Mid Atlantic | 50.72% | 4.91% | 13.26%
Lodging - Mid Atlantic | 12.46% | 5.43% | 2.18%
Food Service - Mid Atlantic | 17.51% | 2.98% | 3.69%
Retail - Mid Atlantic | 31.24% | 6.24% | 8.06%
Classroom / Office Averaged | 39.36% | 6.06% | 9.72%
Office/Food Service/Public Assembly | 28.48% | 9.76% | 10.28%
Campus-wide Geothermal Design |  | 
Parameter | Heating | Cooling
Short-Circuit Factor (Fsc) | 1.04 | 1.04
Part-Load Factor (PLFm) | 1 | 1
Average Heat Transfer to Ground (qa) | -1390309 | -1390309
Block Loads (qlc and qlh) | 17939009 | 16548700
Resistance of Ground, Annual pulse (Rga) | 0.215 | 0.215
Resistance of Ground, Daily pulse (Rgd) | 0.129 | 0.129
Resistance of Ground, Monthly pulse (Rgm) | 0.207 | 0.207
Resistance of Bore (Rb) | 0.09 | 0.09
Undisturbed Ground Temperature (tg) | 53 | 53
Temperature Penalty for Bore Spacing (tp) | 1.8 | 1.8
Heat Pump Inlet Temperature (twi) | 38 | 78
Heat Pump Outlet Temperature (two) | 33 | 85
System Power Input (Wc and Wh) | 111855 | 111855
Required Bore Length (Lc and Lh) | 463653.1 | 220436.7

## Slide 38: Appendix Slides Campus Geothermal
Chart: Pounds of Pollutant per Year
| CO2e | CO2 | CH4 | N2O | NOx | SOx | CO | TNMOC | Lead | Mercury | PM10 | Solid Waste
Electricity | 14790348 | 13940328 | 30515.718 | 328.9577 | 25500.6 | 72846.714 | 7259.1708 | 617.1145 | 1.1815 | 0.28561 | 787.1185 | 1742541
Natural Gas | 468637.4989 | 464827.4379 | 9.5252 | 9.5252 | 422.9168 | 2.408 | 355.4787 | 23.3557 | 0.001905 | 0.00099062 | 32.0045 | 0
  Original Campus
Chart: Pounds of Pollutant per Year
| CO2e | CO2 | CH4 | N2O | NOx | SOx | CO | TNMOC | Lead | Mercury | PM10 | Solid Waste
Electricity | 10709600.5714 | 10094106.2857 | 22096.2449 | 238.1963 | 18464.8286 | 52747.8603 | 5256.3212 | 446.8489 | 0.85554 | 0.20681 | 569.9477 | 1261763.2857
Natural Gas | 398436.7883 | 395197.4648 | 8.0983 | 8.0983 | 359.5649 | 2.0473 | 302.2289 | 19.8571 | 0.0016197 | 0.00084222 | 27.2103 | 0
  Geothermal Redesign
Background Noise Levels | 
Room | Overall dBA
Classroom 120 | 32 dBA
Classroom 121 | 31 dBA
Classroom 122 | 29 dBA
Classroom 246 | 32 dBA
Classroom 247 | 31 dBA
Classroom 248 | 28 dBA
Geothermal Cost Savings |  |  |  | 
Item | Unit Cost | Amount | Units | Savings
RTU's - Quote (20,500, 14,000, 10,725 CFM's) | $ 300,000.00 | 1 | All | $ 300,000.00
RTU Installation | $ 2.00 | 45,230 | CFM | $ 90,460.00
Fin Tubes | $ 75.00 | 1150 | LF | $ 86,250.00
Radiant Heat Panels | $ 100.00 | 80 | Each | $ 8,000.00
 |  |  |  | $ 484,710.00