## Slide 1
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Berkeley, CA
Anderson Clemenceau
Mechanical Option
Penn State A.E. Senior Thesis
April 14, 2015
Leddy Maytum Stacy Architects, Photo by Tim Griffith

## Slide 2
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
ASHRAE Climate Zone 3C
99.6% Heating DB: 37°F
0.4% Cooling DB: 81.8°F
MCWB: 65°F
Google Maps
Leddy Maytum Stacy Architects

## Slide 3
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 4
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Water Source Heat Pump System With 100% Outdoor Air
2 Gas-fired Boilers Provide Hot Water
  900 MBH (Each)
  98% Efficiency
2 Cooling Towers Provide Chilled Water
  100 Ton Capacity (Each)
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 5
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Water Source Heat Pump System With 100% Outdoor Air
2 Gas-fired Boilers Provide Hot Water
  900 MBH (Each)
  98% Efficiency
2 Cooling Towers Provide Chilled Water
  100 Ton Capacity (Each)
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
5 Air Handling Units
3 Constant Air Volume Units
2 Variable Air Volume Units
Paired with Exhaust Fans
Water Source Heat Pumps
Total of 63 Units
Range of Capacity: 0.75 – 3.25 tons
COP: 4.1 – 4.4
EER: 13.7 - 16.0
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 6
Water Source Heat Pump System With 100% Outdoor Air
2 Gas-fired Boilers Provide Hot Water
  900 MBH (Each)
  98% Efficiency
2 Cooling Towers Provide Chilled Water
  100 Ton Capacity (Each)
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
5 Air Handling Units
3 Constant Air Volume Units
2 Variable Air Volume Units
Paired with Exhaust Fans
Water Source Heat Pumps
Total of 63 Units
Range of Capacity: 0.75 – 3.25 tons
COP: 4.1 – 4.4
EER: 13.7 - 16.0
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Radiant Floor
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use
Leddy Maytum Stacy Architects

## Slide 7
Water Source Heat Pump System With 100% Outdoor Air
2 Gas-fired Boilers Provide Hot Water
  900 MBH (Each)
  98% Efficiency
2 Cooling Towers Provide Chilled Water
  100 Ton Capacity (Each)
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
5 Air Handling Units
3 Constant Air Volume Units
2 Variable Air Volume Units
Paired with Exhaust Fans
Water Source Heat Pumps
Total of 63 Units
Range of Capacity: 0.75 – 3.25 tons
COP: 4.1 – 4.4
EER: 13.7 - 16.0
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
 | Area Served | Coverage Area (sqft) | Cooling Cap. (MBH) | Heating Cap. (MBH)
Zone 1 | Courtyard North | 1800 | 27 | 18
Zone 2 | Courtyard South | 2000 | 30 | 20
Zone 3 | Lobby | 3350 | 58 | 30
Radiant Floor
Heating and Cooling Capacity
Serves Lobby and Courtyard Areas – 7,150 sq. ft.
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 8
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Trace 700 Model vs. Real Building
Energy Use
~30% Less Electricity Use
~30% More Gas Use
 | Modeled | Building Capacity
Cooling | 146 Tons | 200 Tons
Heating | 2,200 MBH | 1800 MBH
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 9
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Chart: Boiler - Natural Gas Use
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
 | 2327.8008 | 1711.5842 | 2057.9368 | 1302.2438 | 312.674 | 0 | 0 | 79.2654 | 0 | 128.0989 | 1391.9682 | 2034.6527
Chart: Energy Use by HVAC Equipment Type
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Cooling Tower | 22518.61 | 16842.84 | 21357.59 | 18102.39 | 19534.6 | 17819.94 | 16711.93 | 19235.11 | 15765.92 | 14464.4 | 16952.31 | 19714.2
Tower Fans | 0 | 173.22 | 665.84 | 902.05 | 2591.1 | 4301.41 | 5107.26 | 4930.48 | 5033.13 | 3033.2 | 737.42 | 0
Ceiling Pumps | 13040.58 | 11775.92 | 13052.05 | 12658.99 | 13146.23 | 12762.52 | 13187.45 | 13208.1 | 12778.45 | 13122.31 | 12641.21 | 13037.09
Fans | 13014.01 | 11779 | 14196.38 | 12350.13 | 13654.39 | 13554.85 | 12353.21 | 14238.32 | 12444.29 | 13674.45 | 12982.72 | 12438.86
Trace 700 Model vs. Real Building
Energy Use
~30% Less Electricity Use
~30% More Gas Use
 | Modeled | Building Capacity
Cooling | 146 Tons | 200 Tons
Heating | 2,200 MBH | 1800 MBH
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 10
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Chart: Electricity Use
| January | February | March | April | May | June | July | August | September | October | November | December
Trace Model | 66339 | 54967 | 61112 | 49846 | 51243 | 49130 | 46583 | 53523 | 49541 | 52585 | 55350 | 63847
Existing Building | 76000 | 70560 | 67680 | 64800 | 69600 | 69440 | 77760 | 72320 | 74400 | 76000 | 64000 | 77120
Chart: Boiler - Natural Gas Use
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
 | 2327.8008 | 1711.5842 | 2057.9368 | 1302.2438 | 312.674 | 0 | 0 | 79.2654 | 0 | 128.0989 | 1391.9682 | 2034.6527
Chart: Energy Use by HVAC Equipment Type
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Cooling Tower | 22518.61 | 16842.84 | 21357.59 | 18102.39 | 19534.6 | 17819.94 | 16711.93 | 19235.11 | 15765.92 | 14464.4 | 16952.31 | 19714.2
Tower Fans | 0 | 173.22 | 665.84 | 902.05 | 2591.1 | 4301.41 | 5107.26 | 4930.48 | 5033.13 | 3033.2 | 737.42 | 0
Ceiling Pumps | 13040.58 | 11775.92 | 13052.05 | 12658.99 | 13146.23 | 12762.52 | 13187.45 | 13208.1 | 12778.45 | 13122.31 | 12641.21 | 13037.09
Fans | 13014.01 | 11779 | 14196.38 | 12350.13 | 13654.39 | 13554.85 | 12353.21 | 14238.32 | 12444.29 | 13674.45 | 12982.72 | 12438.86
Trace 700 Model vs. Real Building
Energy Use
~30% Less Electricity Use
~30% More Gas Use
 | Modeled | Building Capacity
Cooling | 146 Tons | 200 Tons
Heating | 2,200 MBH | 1800 MBH
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Existing Systems
Equipment
  Cooling and Heating
  100% OA System
  Radiant Floor
Energy Use

## Slide 11
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 12
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use
VRF Heat Recovery System
Air-cooled Condenser (Outdoor) Unit
Variable-Speed Scroll Compressor
Simultaneous Cooling And Heating
Heat Recovery Between Indoor Units
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
c
c
c
Johnson Controls
Ceiling-Mounted, Ducted Indoor Units
6,000-48,000 Btu/h Capacities
.32 in wg Static Pressure
Johnson Controls

## Slide 13
 | Nominal Size of Outdoor Unit [tons] | IEER | COP
VRF Zone 1 | 26 (10+10+6) | 18.8 | 3.56
VRF Zone 2 | 22 (10+6+6) | 18.8 | 3.61
VRF Zone 3 | 18 (6+6+6) | 19.2 | 3.49
VRF Zone 4 | 28 (8+8+6+6) | 21.2 | 3.87
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
VRF Mechanical Zoning Plan
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
First Floor
Second Floor
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use
Leddy Maytum Stacy Architects
Leddy Maytum Stacy Architects

## Slide 14
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Dedicated Outside Air System (DOAS)
Supplies Filtered, Dehumidified Ventilation Air
Variable-Speed Fan Operation
DX Cooling, Electric Heating
 | Required Airflow [cfm] | Model | DOAS Unit Nominal Airflow [cfm]
VRF Zone 1 | 4,426.47 | JDHA-210 | 2250-5500
VRF Zone 2 | 5,480.2 | JDHA-300 | 3750-8700
VRF Zone 3 | 3,808.54 | JDHA-210 | 2250-5500
VRF Zone 4 | 5,867.72 | JDHA-300 | 3750-8700
Lobby/Reception | 2,503.64 | JDHA-120 | 1500-3550
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 15
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Chart: Utility Costs: WSHP vs. VRF
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
WSHP | 12772 | 10540 | 12719 | 10862 | 16661 | 16155 | 15590 | 17183 | 15358 | 15390 | 10922 | 11472
VRF | 13904 | 11125 | 12414 | 9352 | 13786 | 11899 | 10791 | 12600 | 10997 | 12586 | 10311 | 12250
% Change in Utility Cost - WSHP vs. VRF |  |  |  |  |  |  |  |  |  |  | 
Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
8.86% | 5.55% | -2.40% | -13.90% | -17.26% | -26.34% | -30.78% | -26.67% | -28.40% | -18.22% | -5.59% | 6.78%
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Yearly Utility Cost Change: 14.3%
Yearly Savings: $23,200
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 16
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Life Cycle Cost Analysis
2014 Supplement to NIST Manual 135
Discount Rate: 3%
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Existing System Energy Costs | VRF Energy Costs | Net Savings | Investment | Discounted Payback Period
$4,336,036.32 | $3,718,476.30 | $617,560.02 | $364,300.00 | 20 Years
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 17
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Solar Thermal Water Heating System
Domestic Water Heating
Radiant Floor Space Heating
Analysis: CombiSys
Solar Thermal Water Heating Simulation
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use
Solar Thermal Schematic

## Slide 18
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Solar Thermal Water Heating System
Domestic Water Heating
Radiant Floor Space Heating
Analysis: CombiSys
Solar Thermal Water Heating Simulation
Model Inputs:
Collector Area: 90 m2 (970 ft2)
Collector Performance Characteristics: η0=0.687, a1=1.505 [W/m2-K], a2=0.011 [W/m2-K]
Dom. Hot Water Load: 3 gal/d per occupant, 50 occupants
Space Loss Coefficient: 500 W/K (~1700 Btu/h/°F)
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 19
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Solar Thermal Water Heating System
Domestic Water Heating
Radiant Floor Space Heating
Analysis: CombiSys
Solar Thermal Water Heating Simulation
Model Inputs:
Collector Area: 90 m2 (970 ft2)
Collector Performance Characteristics: η0=0.687, a1=1.505 [W/m2-K], a2=0.011 [W/m2-K]
Dom. Hot Water Load: 3 gal/d per occupant, 50 occupants
Space Loss Coefficient: 500 W/K (~1700 Btu/h/°F)
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Chart: Comparison of Collector Angles
| January | February | March | April | May | June | July | August | September | October | November | December
47 Degree | 69.56 | 84.2492 | 89.3841 | 93.3318 | 98.1969 | 97.3645 | 100 | 100 | 100 | 99.1327 | 91.6012 | 69.2588
37 Degree | 64.1914 | 81.161 | 88.937 | 94.9787 | 99.3082 | 98.9338 | 100 | 100 | 100 | 99.2615 | 88.0501 | 61.4604
27 Degree | 55.513 | 74.9702 | 86.1833 | 95.1237 | 99.5054 | 99.3884 | 100 | 100 | 100 | 99.1131 | 80.314 | 50.3475
Gross Roof Area:
~2,500 sq. ft.
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 20
Model Inputs:
Collector Area: 90 m2 (970 ft2)
Collector Performance Characteristics: η0=0.687, a1=1.505 [W/m2-K], a2=0.011 [W/m2-K]
Dom. Hot Water Load: 3 gal/d per occupant, 50 occupants
Space Loss Coefficient: 500 W/K (~1700 Btu/h/°F)
CombiSys Solar Thermal Simulation
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Chart: Solar Gains vs. Building Loads
| January | February | March | April | May | June | July | August | September | October | November | December
DHW | 3131197.6968 | 2827489.5491 | 3131753.9188 | 3022278.6476 | 3127785.6765 | 3025431.5525 | 3129913.0963 | 3126985.5624 | 3017123.9145 | 3122201.3205 | 3028154.1757 | 3129105.643
Space Load | 14406998.4852 | 9987763.81 | 11683427.3794 | 9602277.158 | 8011792.8411 | 6684981.7355 | 5537563.9535 | 5303149.853 | 4769661.5764 | 6492878.1859 | 9368716.0928 | 13722352.3535
Useful Gain | 11749784.9443 | 11866605.3023 | 13072864.3011 | 12475324.6112 | 11225010.8922 | 10006641.1677 | 9187184.2958 | 9290512.604 | 8456102.1366 | 9953258.5674 | 10996376.4398 | 11605427.6106
Aux Heat | 5126884.649 | 1919546.8932 | 1498921.9228 | 796949.9403 | 188312.4035 | 238177.7383 | 0 | 0 | 0 | 77358.1526 | 984653.989 | 4966504.1661
Avg. Solar Fraction
91%
Avg. Collector Efficiency
24%
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 21
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Chart: Solar Gains vs. Building Loads
Model Inputs:
Collector Area: 90 m2 (970 ft2)
Collector Performance Characteristics: η0=0.687, a1=1.505 [W/m2-K], a2=0.011 [W/m2-K]
Dom. Hot Water Load: 3 gal/d per occupant, 50 occupants
Space Loss Coefficient: 500 W/K (~1700 Btu/h/°F)
CombiSys Solar Thermal Simulation
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 22
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Life Cycle Cost Analysis
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Yearly Cost Savings | Net Savings | Investment | Discounted Payback Period
$3,058.63 | $80,074.93 | ~$75,000 | 25+ Years
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 23
Peak 1-Hour Demand of 150 gal
Constant, Year-Round Load
Alternative Application:
Domestic Hot Water Only
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Chart: DHW Load vs.Useful Gains
| January | February | March | April | May | June | July | August | September | October | November | December
DHW Load | 3129715.464 | 2827537.7959 | 3130396.0252 | 3027933.2058 | 3124338.4662 | 3027338.1551 | 3133799.9888 | 3122847.9422 | 3008251.9641 | 3110467.8756 | 3027578.9474 | 3130053.2746
Solar Gains | 2321147.1993 | 2654733.5728 | 2631444.0051 | 2797977.3507 | 2740144.5666 | 2755955.575 | 2882633.676 | 2932522.1846 | 2918521.5347 | 2860728.3432 | 2530306.1913 | 2503857.1649
Solar Fraction | 85.9385 | 95.1303 | 96.7249 | 98.3071 | 98.6629 | 98.4666 | 100 | 99.9758 | 100 | 99.1529 | 95.1765 | 90.3757
Solar Fraction | Collector Efficiency | Yearly Cost Savings | Investment | Payback Period
96% | 23% | $2,016 | ~$25,000 | 18 Years
Mechanical Depth
Variable Refrigerant Flow System
  Equipment
  Unit Sizing
  Energy Use
Solar Thermal
  Radiant Floor and DHW
  System Sizing
  Energy Use

## Slide 24
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Current Roof Structure
  Structural Steel Framing
  18 Gage Verco W3 Metal Decking
  3-1/2” LW Concrete Topping
Roof Structure Redesign
  Current Structure
  New Design Criteria
  Results
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Verco Decking, Inc.
Current Roof Structure
Max Unshored Clear Span: 15’-7” @3-Span
Allowable Superimposed Load for 11’-0” Span Condition: 207 psf
Typical Framing Plan for South East Roof:
3 Spans @10’-8”

## Slide 25
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
Current Roof Structure
  Structural Steel Framing
  18 Gage Verco W3 Metal Decking
  3-1/2” LW Concrete Topping
Solar Panel Array for DHW and Space Heating
30 Panels at 225 lb/panel
Vertical Pull Force Due To Wind: ~610 lb
Panel Area on Roof: 1,100 sq ft.
Total Additional Load: ~55 psf
Roof Structure Redesign
  Current Structure
  New Design Criteria
  Results
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Vulcraft Deck Manuals
3VLI Composite Deck, LW Concrete Topping
19 Gage, 2” Topping
Self-Weight: 35 psf
Maximum SLL @10’-8” Spans: 105 psf
Arup, San Francisco

## Slide 26
Introduction
Existing Systems
Mechanical Depth
Structural Breadth
Conclusion
The Ed Roberts Campus
Anderson Clemenceau – Mechanical Option
Senior Thesis 2015
Variable Refrigerant Flow System
First Cost: $364,300
Yearly Energy Savings: $23,200
Payback Period: 20 Years
Conclusion:
Not Recommended For A Complete Renovation
Could Be Considered For New Construction
Solar Thermal Water Heating System
Two Options:
Space Heating and DHW
  First Cost: $75,000
  Payback: 25+ Years
DHW Only
  First Cost: $25,000
  Payback: 18 Years
Conclusion:
Not Recommended
Could More Economical In Different Climate Conditions