## Slide 1: DENVER POLICE DPT. CRIME LAB
jackie eury
senior thesis presentation
lighting | electrical
15 april 2015
Notes: Hey everyone, my name is Jackie eury, I’m a 5th year lighting/electrical student and this is my thesis presentation on the Denver Police Department Crime lab.

## Slide 2
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
Notes: First, I wanted to run through today’s agenda. I will be touching on two of my spaces (lobby and south plaza) in the lighting depth, go over a pv array design in my electrical depth, and look for financial and structural support for the installation in my two breadths. Let’s jump right into the basics (click)

## Slide 3
building statistics
building location
location | denver, colorado
occupant | denver police department
type | laboratory
size | 60,000 gsf
constructed | march 2011 – july 2012
actual cost | $28 million
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
Notes: The Denver crime lab is located in the center of Denver in a zoned as the golden triangle district. Occupied by crime lab, and usually operates until 3 am Monday through Friday. It is a laboratory that houses 3 stories and around 60,000 sf. (click) The crime lab stands just north of the Denver police department and a large parking deck. With logistics out of the way, it’s time to get into the (click) lighting depth

## Slide 4
l i g h t i n g d e p t h
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion

## Slide 5
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
i d e n t i t y
denver crime lab
concept
investigation
mystery
trials
discovery
teamwork
analysis
research
justice
chemistry
Notes: When searching for a concept, I thought of the people that occupy the crime lab. People that are constantly researching, studying, and analyzing evidence. Their work leads to the solution of a case, the conviction of a criminal, and the peaceful mind of a victim. What they are ultimately doing is discovering someone’s I D E N T I T Y. It could be a drop of blood left at a crime scene, a physical feature observed by a witness, or a fingerprint on a murder weapon. All of these components are ways to discover a person’s identity. This concept, along with the architecture and function of each space influence the lighting design. With that in mind, let me introduce you to the lobby.

## Slide 6
l o b b y
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
orientation
plan
section
Notes: The lobby is located in the center of the building with occupants entering through the south atrium. The north atrium also reaches 3 floors and instead of reception, has a lounge space and staircase. Connecting the two is a 12’ high corridor. Within the lobby are two atriums that carry through the three stories of the building and accommodate corridors. An elevator and large staircase help transition employees throughout the building.
Area | 1903 ft2
Ceiling Height | 12’-0,” 46’-0”
Room Length | 71’-0”
Room Width | 51’-0”
Ceiling | Perforated Metal Panels
Walls | Gypsum, Composite Panels, Wood Panels
Floor | Terrazzo, Carpet

## Slide 7
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
concept
core
beginning
d n a
Notes: Just as a strand of DNA becomes the genetic material of a person’s beginning, the Lobby represents the start of the building and is truly its core. There are traditional (double helix) and new ways (dna fingerprint) to analyze DNA.

## Slide 8
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
qualitative criteria
aesthetics
Task | Eh (lux) | Avg:Min
Transition | - | -
Day Night | 100 50 | 4:1 4:1
Reception | 150 | 4:1
Lounge | 150 | 2:1
quantitative criteria
lighting power density
Space | Allowance (W/ft2)
Lobby | 1.10
illuminance levels
transition
welcoming
bright
Notes: As the main entrance space, and first visually impactful room in the crime lab, the lobby should be aesthetically pleasing.
Power density.

## Slide 9
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
denver crime lab
reflected ceiling plans
first floor
third floor
Notes: spacing between rl2a, rl2b
dimming

## Slide 10
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
renderings
plan view
first floor
Notes: Entrance. Brightly lit. Upon turning away from the desk a visitor’s eyes would be drawn to the wood wall, which showcases a dna fingerprint design using 3 different sizes of led panels.
When walking into the Denver Crime Lab, a visitor is immediately drawn to the reception desk, which is brightly illuminated. From there, one can be guided to the elevator or corridors through recessed linear LED panels that create a line of transition. However, one may be drawn to the exposed staircase via the DNA fingerprint design incorporated in the wood-paneled wall. This LED design is intended to be eye-catching, and can be seen upon turning away from the reception desk. In contrast to the wall, there is a DNA helix inspired pendant that hangs in the North Atrium above the lounge. The helix, which is composed of bare fluorescent lamps represents the older idea of DNA whereas the LED DNA wall represents the leaps technology has made in crime investigation and lamp type together.

## Slide 11
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
renderings
plan view
first floor
second floor
Notes: Upon entering the lounge you are greeted with the next focal point, a double-helix inspired pendants. The 12 pendants twist around in a spiral to the 3rd floor of the crime lab atrium. Giving viewers who decide to rest in the lounge sufficient light and

## Slide 12
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
quantitative data
Illuminance average | 206 lux
average/minimum | 3.7:1
lighting power density | 1.0 w/sf
elumtools calculation
Chart: 
| Illuminance (lux)
Recommended | 150
Achieved (Avg.) | 206
Notes: An Elumtools calculation can be shown on the right.

## Slide 13
s o u t h p l a z a
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
plan
orientation
Notes: 5500 sf

## Slide 14
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
denver crime lab
concept
individuality
uniqueness
one of a kind
f i n g e r p r i n t
Notes: The identity for the south plaza was inspired by individuality, one of a kind uniqueness.

## Slide 15
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
qualitative criteria
relaxation
quantitative criteria
lighting power density
illuminance levels
safety
Task | Eh (lux) | Ev (lux) | Avg:Min
Transition – Plaza | 6 | 2 | 5:1
Space | Base Allowance (W) | Allowance (W/sf) | Square Footage | Total Allowance (W)
South Plaza | 1300 | 0.2 | 5500 | 2400
Space | Lighting Zone | Allowance (LM/sf)
South Plaza | LZ4 | 7.5
model lighting ordinance
Notes: performance method, Flynn modes

## Slide 16
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
denver crime lab
site plan
Notes: linear form in front of the entrance

## Slide 17
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
denver crime lab
renderings
plan view
site
Notes: Intimate setting is created with nonuniform light levels

## Slide 18
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
quantitative data
Illuminance average | 15 lux
average/minimum | 21:1
total watts | 1848 W
total site lumens | 18,552
lumens/sf | 3.37
elumtools calculation
Chart: 
| Illuminance (lux)
Recommended | 6
Achieved (Avg.) | 15

## Slide 19
e l e c t r i c a l d e p t h
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
Notes: National renewable energy laboratory

## Slide 20
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
system advisor model (sam)
modules
Manufacturer | SunPower
Nominal Efficiency | 19.19%
Maximum Power | 414.8 Wdc
Number of Cells | 128
Length | 7'-0"
Width | 3'-3"
Number of Panels | 240
Manufacturer | Satcon Technology Corp.
CEC Weighted Efficiency | 96.24%
Maximum Power (DC) | 104 kWdc
Maximum Power (AC) | 100 kWac
Nominal AC voltage | 480 V
Number of Inverters | 1
inverter
Notes: Desired array size of 100kwdc to help power lighting panel for south plaza
Dc/AC ratio of 1
240 modules were used
Modules
Monocrystalline > poly or thin film
19.2% efficiency
7’x3’ panel

## Slide 21
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
module layout
solar angles
penthouse
analysis summary
Annual Energy Production | 160,128 kWh
Performance ratio | 0.86
Electricity Cost without system | $92,605
Electricity Cost with system | $77,440
Initial Cost | $646,431
Payback Period | 50 + Years
Number of Panels | 240
total savings | $15,165
Notes: The modules were laid out on the east side of the roof since the west side houses the penthouse (CLICK). The angle and spacing of the panels was determined by where the sun’s altitude was at noon on the Fall Equinox. The sun’s altitude should fall between the low angles of winter and the high angles of summer in Denver so there will be a better chance of maintaining an average amount of sunlight for the year. In summary, the total savings that the crime lab would receive from the photovoltaic array would be $15,000, but the payback of more than 50 years and initial cost of 646,000 would deem the installation unfeasible.

## Slide 22
c o n s t r u c t i o n b r e a d t h
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
Notes: In my construction breadth I will be discussing a cost, schedule, and energy saving analysis.

## Slide 23
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
cost analysis
RS MEANS 2015 COST DATA |  |  |  |  |  | 
ITEM | CREW | QUANTITY | 2015 BARE COSTS |  |  | 
 |  |  | MATERIAL | LABOR | TOTAL | INCLUDING OVERHEAD & PROFIT
ALT. ENERGY SOURCE, SUNPOWER PHOTOVOLTAIC MODULE, 415 WATT, 73 VOLTS | 2 | 240 | 1,785.00 | 109.00 | 454,560.00 | 522,744.00
SATCON CORP. DC TO AC INVERTER, 480 V, 100 KW | 1 | 1 | 41,688.00 | 219.00 | 41,907.00 | 48,193.05
PV COMPONENTS, COMBINER BOX, NEMA 3R ENCLOSURE | 1 | 1 | 191.00 | 109.00 | 300.00 | 345.00
FUSE, 15 A FOR COMBINER BOX | 1 | 40 | 18.75 | 10.95 | 1,188.00 | 1,366.20
PV RACK SYSTEM, ROOF, NON-PENETRATING BALLAST, 1 PANEL | 1 | 240 | 895.00 | 23.50 | 220,440.00 | 253,506.00
total cost | $826,154.25
schedule
ITEM | CREW | DAILY OUTPUT | LABOR HOURS | QTY. | HOURS | DAYS
ALT. ENERGY SOURCE, SUNPOWER PHOTOVOLTAIC MODULE, 415 WATT, 73 VOLTS | 2 | 8 | 1 | 240 | 120 | 15.00
SATCON CORP. DC TO AC INVERTER, 480 V, 100 KW | 1 | 2 | 4 | 1 | 4 | 0.50
PV COMPONENTS, COMBINER BOX, NEMA 3R ENCLOSURE | 1 | 4 | 2 | 1 | 2 | 0.25
FUSE, 15 A FOR COMBINER BOX | 1 | 40 | 0.2 | 40 | 8 | 1.00
PV RACK SYSTEM, ROOF, NON-PENETRATING BALLAST, 1 PANEL | 1 | 30.5 | 0.525 | 240 | 126 | 15.75
schedule duration | 1 month
Notes: RS means green building 2015 were used except for the values of the module and inverter. Using 2 crews for the installation of the modules and 1 for the rest of the project, the photovoltaic array would cost 826,000 and take a month to complete. This value is 180,000 different from SAM’s estimate, but I attributed this to RS MEANS more accurate method of estimating labor.

## Slide 24
s t r u c t u r a l b r e a d t h
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
Notes: My structural breadth focuses on the pv array installation on the roof.

## Slide 25
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
roof analysis
deck type
composite | 2VLI20
roof | 1.5B20
module layout
Notes: The crime lab’s roof is made of composite deck and roof deck. There are more than 3 spans, with the largest span being 6’0.” (CLICK). The module layout sits on both types of deck. The composite deck portion of the roof is highlighted in blue and is composed of Vulcraft’s 2” 20 Gage deck. The roof deck is 1.5” 20 Gage deck. The composite deck supports 100 modules while the roof deck supports 140.

## Slide 26
live
minimum live load | 30 psf
dead
rigid insulation | 2 psf
superimposed dead load | 10 psf
composite deck self-weight | 1.97 psf
roof deck self-weight | 2.14 psf
module weight | 56 lbs
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
loads
calculations
composite deck
roof deck
snow load | 20 psf
WTL = < 400 psf √
WTL = < 111 psf √
Notes: minimum live load controls. was larger than snow load. The weights of the deck were found in the Vulcraft manual and the per square foot of the modules was found by taking the weight of the module and multiplying by the panels and dividing by the square feet it rests on. The composite deck more than adequately supported the 46 psf total load and the roof deck was a little under half the requirement via Vulcraft. In conclusion, the roof could support the photovoltaic array with no problems.

## Slide 27
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion
lighting
electrical
construction
structural
c o n c l u s i o n
Notes: Speaking of conclusions, we have just arrived at the end of my presentation. Lighting was explored through DNA and fingerprints, both important parts of a person’s identity. My electrical depth analyzed a pv array that would be able to supply 100 kw, but may not be financially feasible. The construction breadth confirmed this initial electrical analysis, but should it proceed the installation should last a month. And lastly, my structural breadth supported the PV array installation, even if it wasn’t supported financially. …The Denver Crime Lab is a building that seeks justice through careful forensic investigating (and specially placed lighting) while maintaining its own (click) identity. (click) thank you.

## Slide 28
t h a n k y o u
a special thanks:
Mom & Dad
SmithgroupJJR
Denver Police Department
Shawn Good
AE Faculty & Staff
Friends and Colleagues
Nicolas Cage
denver crime lab
introduction
lighting depth
lobby
south plaza
electrical depth
photovoltaic array
construction breadth
structural breadth
conclusion

## Slide 29
support | lobby

## Slide 30
support | lobby

## Slide 31
support | plaza

## Slide 32
support | plaza

## Slide 33
support | structural

## Slide 34
denver crime lab
 | 5am | 6am | 7am | 8am | 9am | 10am | 11am | 12pm | 1pm | 2pm | 3pm | 4pm | 5pm | 6pm
Jan | 100 | 100 | 66.6262 | 41.4284 | 30.9819 | 26.1548 | 24.3441 | 24.0069 | 25.4262 | 31.477 | 43.3256 | 66.0323 | 100 | 100
Feb | 100 | 100 | 38.6662 | 23.2976 | 17.1339 | 14.3545 | 13.1805 | 12.6909 | 13.6214 | 17.108 | 25.4686 | 43.101 | 73.5851 | 100
Mar | 100 | 9.15711 | 4.28353 | 2.24689 | 1.49688 | 1.17057 | 0.832361 | 0.978999 | 0.923388 | 2.54405 | 7.19344 | 17.0431 | 57.1892 | 100
Apr | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.597934 | 4.19657 | 11.1939 | 29.4424 | 100
May | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.195979 | 3.21961 | 8.33564 | 21.2989 | 100
Jun | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018403 | 2.41565 | 6.35199 | 15.5866 | 100
Jul | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007914 | 2.28821 | 6.54035 | 15.3936 | 100
Aug | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.216182 | 3.30129 | 9.24263 | 21.5792 | 100
Sept | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48456 | 5.83348 | 15.1104 | 60.0621 | 100
Oct | 100 | 36.4335 | 18.6618 | 12.2612 | 9.63929 | 8.423 | 7.85318 | 8.19911 | 9.06049 | 14.0736 | 23.5467 | 47.9667 | 100 | 100
Nov | 100 | 100 | 45.3173 | 30.6975 | 24.2614 | 21.5754 | 20.669 | 20.7049 | 23.4766 | 30.9598 | 45.2631 | 73.2618 | 100 | 100
Dec | 100 | 100 | 65.4185 | 43.0801 | 33.367 | 29.0345 | 27.2614 | 27.3223 | 29.9461 | 37.6982 | 52.2935 | 79.0083 | 100 | 100
shading loss
support | electrical
Notes: Within SAM I also conducted a shading study which analyzes how much energy is lost based on the spacing of the modules. As you can see in the table, March through September are relatively unshaded while the low anlge winter months lead to the most loss (but generally not more than 35%).

## Slide 35
denver crime lab
energy analysis
annual kWh reduction | 10,000 kWh
annual savings | $600.00
support | construction
Notes: talk about hours, .06/kwh

## Slide 36
citations
IECC 2012
The Lighting Handbook, 10th edition
Vulcraft Manual
Revit 2015
RS Means Green Building 2015
images
Double Helix. Web.
Http://www.Ummo-sciences.Org/en/a037.Htm
Figure 2. 2000. Centers for disease control and prevention. By chang gung. Web.
M. 1931. By fritz lang. Web.
Photograph of author. 2012. Rotterdam. Ciencia hoje. Web.

## Slide 37
YEAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAA